## Slide 1: Technical I Rotating Equipment Part I
Fans & Blowers
Development of a 21st Century Industrial Process Operations Program is supported by the National Science Foundation under Grant No. 1700558. Any opinions, findings, and conclusions or recommendations expressed on this site are those of the authors and do not necessarily reflect the views of the National Science Foundation.

## Slide 2: Rotating equipment
What is rotating equipment
  Generally refers to mechanical devices used to transfer fluids of various types
    Gas, vapor or liquid
  Other types of rotating equipment
    Centrifuges
    Rotary screens
    Kilns

## Slide 3: Two important concepts
Centrifugal force
  The force resulting from circular motion of a body
    It converts the energy provided by a prime mover (i.e. electric motor, steam turbine, or gasoline engine) to energy within the fluid being Pumped
    https://www.youtube.com/watch?v=z3BSkMj1wLc
Positive Displacement
  The system which processes a defined volume of fluid per revolution
  A positive displacement device operates by alternating filling a cavity and then displacing a given volume of fluid. A positive displacement device delivers a constant volume of fluid for each cycle independent of discharge pressure or head.

## Slide 4: Displacement
https://www.youtube.com/watch?v=4OJTN0M1DBk

## Slide 5: Industrial Fans & blowers
Used to transfer large to very large quantities of gas at low pressure (<50PSI)
A Lot of people use the terms “fan”, “blower” and “compressor” interchangeably
  Evan though there are some significant differences

## Slide 6: Industrial fans
Fans
  Generally slow to medium speed
    100 – 1800Rpm (most common 300-500rpm)
  Outlet Pressures <5PSI
  Can be used to pull a small partial vacuum
Fan Types
  Radial
  axial

## Slide 7: radial Fans
Radial (wheel) fans
Large impeller (wheel)
Works on centrifugal force
Typical applications
  Heater & Boiler induced draft (ID) & Forced draft (Fd)
  boiler over fire air (ofa)
  Pollution control air handling

## Slide 8: Generic Boiler arrangement

## Slide 10: Fan design
Two basic fan designs
  Over hung impeller
  Center hung impeller

## Slide 11: Over hung

## Slide 12: Center hung

## Slide 13: Fan Impeller Design

## Slide 14
https://www.youtube.com/watch?v=N3rQEREzYWU

## Slide 15: Centrifugal Performance curve

## Slide 16: Centrifugal fan performance curves

## Slide 17: radial Fan flow control
Radial Fan Gas flow rate controlled by two methods
  Fan speed
  Dampers
    Dampers are “control valves” utilized in low pressure, high volume gas flows.
    generally always allow some minimum flow arrangement
      Design
      Travel stop to prevent complete closure
    Dampers can be installed on either the inlet or outlet of the fan
  Or a combination of both Speed & Damper

## Slide 18: Dampers

## Slide 19: axial Fans
Axial fans
Large blades
Generally very slow <500rpm
Works on “blade pitch” concept
  Propeller
Typical applications
  Air handling
  Cooling towers
  Fin-fan heat exchangers

## Slide 21
https://www.youtube.com/watch?v=QA2M0z-iA30

## Slide 22: axial Fan flow control
axial Fan Gas flow rate controlled by three methods
  Fan speed
  Fan blade pitch
  Dampers
    Dampers (if used) generally installed on the opposite side as the drive unit
  Or some combination of the three

## Slide 24: Common Fan operating issues
Dirt/moisture/icing
  Dirt/moisture/ice accumulates on the blades
    Erosion of blades
    Vibration
    Can lead to “loss of mass” event
    Increases weight
    Requires more energy input
    Reduces efficiency
Balance/vibration issues
Bearing failure
Corrosion
Metal fatigue

## Slide 25: Common Fan operating issues

## Slide 26: Loss of mass event

## Slide 28: Common damper operating issues
Dampers
  Loss of or poor control
    Actuator malfunction
    Sloppy or broken linkages
    Poor or no maintenance
  Stuck
  plugged
Filters
  Plugging
  Poor maintenance
corrosion

## Slide 29: Industrial blowers
Blowers
Typical pressures from vacuum to ~50PSI
  Industrial; Most common use is to create a vacuum (vacuum pump)
Lower volume
Works on positive displacement
  Most common is the Lobe style
Typically high speed
  2500-10000 RPM (5000- 8800 RPM very common)
Typical applications
  PNP
  Refining
  Chemical manufacturing

## Slide 30: Industrial blowers

## Slide 31: Industrial blowers

## Slide 32: Blower flow control
Blower flow rate normally controlled by two methods
  Blower speed
  Dampers
    Often called “vacuum breakers”
    The system design should always have some method of minimum flow
      System Design
      Travel stop to prevent complete closure
    installed on the inlet of the blower

## Slide 33: Common Blower operating issues
Dirt/moisture
  Dirt/moisture accumulates on the rotors
    Vibration
    Erosion of rotors
    Increases weight
    Requires more energy input
    Reduces efficiency
    Loss of seal
Balance/vibration issues
Bearing failure
Corrosion
Damper issues

## Slide 34: ISA Symbols
Fans
Blowers