## Slide 1: Rotating equipment Part IV
Pump Operational Considerations
Development of a 21st Century Industrial Process Operations Program is supported by the National Science Foundation under Grant No. 1700558. Any opinions, findings, and conclusions or recommendations expressed on this site are those of the authors and do not necessarily reflect the views of the National Science Foundation.

## Slide 2: Key Process Terms
Flow: A Measurement of the Quantity of a Product “Passing a Specific Point, in a Specific Time Period, utilizing a Specific Unit of Measurement”.
  GPM, LPM, M3/HR
Pressure =force/area
  PSI, Kg/cm2, Bar, h-ftH2O
Pressure: In the pump world, we use feet of head {h(ft) or h-ft} for pressure measurement.
  Water at standard conditions (60F): 1psi=2.31 feet or 1ft=.433PSI

## Slide 3: Key Process Terms
S.G. (Sg): specific gravity of the liquid
  The ratio of the weight of a specific volume of fluid compared to water. (s.g. H2O = 1 @ 60F)
    By definition density is ρ=mass/volume
    e.g.: #/ft3
  Varies as a function of temperature
  Some people will call this fluid “density”

## Slide 4: Key Process Terms
Viscosity
  The viscosity of a fluid is a measure of its resistance to gradual deformation by shear stress or tensile stress. For liquids, it corresponds to the informal concept of "thickness".
  For example, honey has a much higher viscosity than water.
  cp, SUS, cST

## Slide 5: Static Head (elevation head)
Static Head / Static Pressure is due to the height and weight of a fluid and it is measured at it’s lowest point.
The higher the reservoir level, the higher the pressure.
What is the pressure produced at the bottom of each tank by the static heads?
(Hint: Head (ft of water) = (psi *2.31)/S.G.)

## Slide 6: Static Head (elevation head)

## Slide 7: Static Head (elevation head)
Is the static pressure the same or different in these containers? Which has the most? Which as the least?
Height is 10’

## Slide 8: Static Head (elevation head)
Is the static pressure the same or different in these containers?
Height is 10’
WHY IS THIS IMPORTANT??

## Slide 9: Static Head – Why is it important?
This is important since in complex piping systems it will always be possible to know the pressure at the bottom if we know the height
  i.e. designing piping systems

## Slide 10: Key Process Terms
Velocity
  The Velocity of an object is the rate of change of its position with respect to a frame of reference, and is a function of time.
  ft/s, m/s,
Friction
  Friction is the force resisting the relative motion of solid surfaces, fluid layers, and material elements sliding against each other.
  Ff

## Slide 11: Friction Energy
Friction energy is the energy that is lost to the environment due to the movement of the liquid through pipes and fittings in the system.

## Slide 12: Key Pump Terms
Pump Priming
Pump Curves
  The graphical representation of a pumps flow and pressure capabilities
  Provided by OEM
Minimum Flow Required
NPSH: Net Positive Suction Head
BHP: Brake Horsepower
Pump Efficiency
BEP: Best Efficiency Point
System Hydraulics
TDH: Total differential (developed) head in feet of fluid pumped

## Slide 13: Pump Priming
Priming is the process in which the impeller of a centrifugal pump will get fully sub-merged in liquid without any air trap inside.
  If not fully sub-merged air may be stuck in the eye of the impeller creating a air pocket and blocks flow,
  Vent the air, insure a flooded suction and restart pump
Centrifugal pumps are not normally self priming
Positive Displacement pumps are generally self priming.
  There is a maximum for all pumps depending on pump design and fluid conditions
  How is this accomplished?
    Soda straw example
Notes: Centrifugal pumps are designed to pump liquids not gases. Any centrifugal pump (even a self-priming pump) will not start pumping unless at least the first stage (such as in a multistage vertical pump) is full of liquid. When pumping a liquid with an excessive amount of entrained air, the air/gas tends to be centrifuged inward towards the eye of the impeller, eventually blocking any liquid flow through the pump (air binding it). If this only happens occasionally, the pump has a positive suction pressure (flooded suction), and the flow stoppage can be quickly detected, stopping and restarting the pump can clear up the air binding.

## Slide 14: Generic Centrifugal Pump Curve

## Slide 15: Specific Equipment Pump Curves

## Slide 16: Key Pump Terms
Minimum Flow Required
  The quoted minimum flow for continuous operation is usually called “Minimum Continuous Stable Flow” (MCSF).It is the flow below which the pump should not be operated continuously.
    S. Gopalakrishnan; paper titled, “A New Method for Computing Minimum Flow,” Proceedings of the Fifth International Pump Users Symposium; Texas A&M University, May 1988
  Ref: Recirc Flow, Min Flow
  Should be provided by OEM
  Can be estimated by user
Operating below this point will damage the pump

## Slide 17: Minimum Continuous Stable Flow

## Slide 18: Minimum Continuous Stable Flow

## Slide 19: Pump Terms: NPSHR
NPSHR :Net Positive Suction Head (required)
  The minimum positive suction head required at the pump inlet to prevent pump issues (cavitation)
  Function of pump design, flow & pressure
  Provided by pump OEM

## Slide 20: Pump Terms: NPSHA
NPSHA :Net Positive Suction Head (available)
  The actual net positive suction head available at the inlet to the centrifugal pump.
  Combines the effects of:
    Total static head
      supply elevation, liquid level and atmospheric pressure or vessel pressure (if any)
    Inlet piping pressure drop
      the dynamic head loss of the suction piping. (calculated)
    Fluid properties
      e.g.: S.G, viscosity & temperature (vapor pressure)
Notes: Imellers and propellers baldes move through a fluid, low pressure areas are formed as the fluid accelerates around and moves past the blades. The faster the blades move, the lower the pressure around it can become. As it reaches vapor pressure, the fluid vaporizes and forms small bubbles of gas. This is cavitation. When the bubbles collapse later, they typically cause very strong local shock waves in the fluid, which may be audible and may even damage the blades.
Impellers – go so fast that it lowers the pressure in the impeller on the trailing edge. Water bubbles trail, leading edge of the enxt blades the bubble causing it to collapse.
Formation and subsequent collapse of vapor bubbles due to water velocity and thus dynamic pressure getting so high that static pressure drops below the saturation pressure for the temperature for the temp of the fluid.

## Slide 21: NPSHR

## Slide 22: NPSHR

## Slide 23: Pump Terms:
Efficiency: pump efficiency (from the pump curve)
BHP: pump brake horsepower (from the pump curve)
  BHP: GPM*TDH*SG/(3960*Eff)
BEP: Pump Best Efficiency Point (from the pump curve)
  Function of pump & impeller design
  Provided by OEM

## Slide 24: Efficiency, BEP
Best efficiency point = operating point
Pump efficiency is defined as the ratio of the power imparted on the fluid by the pump in relation to the power supplied to drive the pump.
Its value is not fixed for a given pump, efficiency is a function of the discharge and therefore also operating head.
Efficiency can decline with wear
Another term you’ll hear: “Slip or Slippage”
  Percent fluid recirculation in the pump.

## Slide 25: Efficiency, BHP, BEP

## Slide 26: Efficiency, BHP, BEP

## Slide 27: System Hydraulics
The calculated/actual total resistances to flow which must be overcome by the pump as a function of flow.
  e.g.: required delivery pressure, elevation change, pipe friction, changes in viscosity, temperature, control valve DP, etc.
Total Differential (Developed) Head (TDH)

## Slide 28: Total Differential Head (TDH)
TDH = Static Head + Friction Head
Total Differential Head = (Hds-Hss) +Hfd +Hfs + Hc
Friction Head: All friction loss through pipes, valves, etc
Hfd = Discharge Friction Head
Hfs = Suction Friction Head
Hc = any added pressure vessels on discharge (cyclones, Pressured tanks, etc.)

## Slide 29: Total Differential Head (TDH)

## Slide 30: Static Head
Static Head = Discharge Static Head (Hds) – Suction Static Head (Hss)

## Slide 31: Calculating Friction Loss
Discharge friction head (Hfd)= # ft of water based on:
Suction friction head (Hsf) = # ft of water based on:
  Velocity of liquid
  Length of pipe
  Diameter of pipe
  Material of pipe
  Type of liquid
  Valves
  Elbows
  Etc.

## Slide 32: Calculating Friction Loss
Hc = any added pressure vessels on discharge (Pressurized vessels, cyclones, etc.)

## Slide 33: Pump Curve
The system curve represents the pressure needed at different flow rates to move the product through the system
The Pump’s Operating Point shows the head required to make the liquid flow through the piping system.

## Slide 34: Pump Curve
System Curve will move depending TDH and change in the system
  Valve is shut
  More piping is added
  Friction change
  Static change
  Etc.

## Slide 35: Pump Curve
Pump Curve will only move for a few conditions (not a sudden change):
  Wear in impeller
  Change in rotational speed
  Change in impeller diameter
  Change in liquid viscosity

## Slide 36: System Hydraulic Analysis
TDH
Q
System Curve

## Slide 37: System Hydraulic Analysis
TDH
Q
System Curve
Centrifugal pump performance curve

## Slide 38: Positive Displacement Pump Curve

## Slide 39: Pump Troubleshooting

## Slide 40: Cavitation
Vapor Pressure
  It is the pressure absolute at which a liquid, at a given temperature starts to boil or flash to a vapor.
  In Rocky MTN NP at elevation of ~12,000 feet, water boils at a lower temperature at this altitude because the atmospheric pressure is lower.

## Slide 41: Cavitation
Defined as the rapid formation and collapse of vapor bubbles in a liquid, due to dynamic action, and resulting in damage to the surface of solid boundaries.
Occurs when a localized dynamic pressure acting on a liquid falls below the vapor pressure of the liquid, vapor bubbles form, then with the subsequent increase in static pressure the vapor bubble collapses creating a microjet of fluid impacting the boundary surface causing fatigue and damage.
Notes: Impellers and propellers blades move through a fluid, low pressure areas are formed as the fluid accelerates around and moves past the blades. The faster the blades move, the lower the pressure around it can become. As it reaches vapor pressure, the fluid vaporizes and forms small bubbles of gas. This is cavitation. When the bubbles collapse later, they typically cause very strong local shock waves in the fluid, which may be audible and may even damage the blades.
Impellers – go so fast that it lowers the pressure in the impeller on the trailing edge. Water bubbles trail, leading edge of the enxt blades the bubble causing it to collapse.
Formation and subsequent collapse of vapor bubbles due to water velocity and thus dynamic pressure getting so high that static pressure drops below the saturation pressure for the temperature for the temp of the fluid.

## Slide 42: Cavitation Cause #1
NPSH available > NPSH required (no cavitation)
NPSH available < NPSH required (cavitation will occur)
https://www.youtube.com/watch?v=U-uUYCFDTrc
Notes: Imellers and propellers baldes move through a fluid, low pressure areas are formed as the fluid accelerates around and moves past the blades. The faster the blades move, the lower the pressure around it can become. As it reaches vapor pressure, the fluid vaporizes and forms small bubbles of gas. This is cavitation. When the bubbles collapse later, they typically cause very strong local shock waves in the fluid, which may be audible and may even damage the blades.
Impellers – go so fast that it lowers the pressure in the impeller on the trailing edge. Water bubbles trail, leading edge of the enxt blades the bubble causing it to collapse.
Formation and subsequent collapse of vapor bubbles due to water velocity and thus dynamic pressure getting so high that static pressure drops below the saturation pressure for the temperature for the temp of the fluid.

## Slide 43: NPSH Cavitation Telltales
Cavitation from NPSH issues will show up on the operator interface as:
  Unstable flow readings
  Unstable pressure readings
Locally as:
  Loud noisy pump operation
  Unstable flow readings
  Unstable pressure readings
  Elevated temperature

## Slide 44: Cavitation Cause #2
Cavitation can also be caused by the pump outlet being excessively restricted or blocked.
  Called “deadheading”
Deadhead cavitation is self propagating:
  Cavitation causes heat
  Heat raises the vapor pressure
  Elevated vapor pressure creates more cavitation.
  And on… and on…..

## Slide 45: Deadhead Cavitation Telltales
Cavitation from deadheading issues will show up on the operator interface as:
  Low/No flow
  High pressure
Locally as:
  Loud noisy pump operation
  Low flow
  Operating pressure above normal
  Elevated temperature

## Slide 46: Cavitation - Problems
Pitting damage to the impeller and/or casing
  Always show up as a rough “sintered” appearance.
Loud noises (pumping gravel)
Vibration
  Over 100 “g’s”
Mechanical seal leakage
Loss of pump efficiency
Bearing failure
Shaft breakage
Piping failure

## Slide 47: Cavitation- impeller erosion

## Slide 48: Cavitation- impeller pitting

## Slide 49: Cavitation – How to get rid of it?
Verify suction and outlet valves are open and operating properly.
  Pump isolation valves should always be open and verified open prior to attempting pump start up
Verify there are no issues downstream.
Raise the NPSHA
  Raise the liquid level in the supply vessel
Reduce temp of process liquid
Use a different pump
Divide flow between two pumps
Improve suction piping (reduce piping friction)
Pressure the supply tank
Eliminate suction valves (Maintenance Issue)
Sometimes we just have to live with it (select impeller material that is more resistant to wear)

## Slide 50: Problem: Troubleshooting Line Plugging
Causes
  Dewatering
  Low velocity (below settling velocity)
  Entrained air
  Sudden slug of material
  Sump vortex
  Air leaks

## Slide 51: Problem: Troubleshooting Line Plugging
Solutions?
  Fix the cause of dewatering
  Increase flow
  Decrease line size
  Control sump level
  Vortex breakers
  Sump design (top hat, boil box, etc.)

## Slide 52: Problem: Inadequate Flow
Causes??
  Line scaling
  New system restriction
  Entrained air
  Cavitation
  Change in feed
Notes: Jig Rocks like at Mag

## Slide 53: Problem: Inadequate Flow
Solutions??
  Remove Scaling
  Speed up pump
  Replace with larger pump
  Increase NPSH

## Slide 54: Problem: Loss of Flow
Causes??
  Air bubble: entrained air
  Worn parts
  Plugged line, sanded up
  Valve closed
  Piping changes

## Slide 55: Problem: Loss of Flow
Solutions??
  Replace Parts
  Clear Line
  Open Valve

## Slide 56: Problem: Packing failure
Causes??

## Slide 57: Problem: Packing failure
Causes??
  Contaminated seal water
  Low pressure seal water
  Interruption in seal water
  Sleeve wear
  Packing wear
  Stuffing box wear
  Lantern ring wear
  Impeller Adjustment

## Slide 58: Problem: Packing failure
Solutions??
  Analyze seal water
  5 psig above discharge pressure
  Hard coated sleeves
  Replace or adjust packing
  Replace stuffing box
  Replace lantern ring

## Slide 59: Questions?