## Slide 1: Welcome to: The Wonderful World of Valves
Development of a 21st Century Industrial Process Operations Program is supported by the National Science Foundation under Grant No. 1700558. Any opinions, findings, and conclusions or recommendations expressed on this site are those of the authors and do not necessarily reflect the views of the National Science Foundation.

## Slide 2: Valves
What is a valve?
A valve is a device that regulates, directs, or controls the flow of a fluid by opening, closing, or partially obstructing the fluid path.
A valve is nothing more than a variable orifice.

## Slide 3: Valve Classifications

## Slide 4: Pressure Safety Valves (PSV)
AKA: Pressure Relief Valves
Purpose:
  PSV’s provide the last line of protection for a process facility’s vessels/tanks/piping from CATASTROPHIC failure from OVER and/or UNDER pressurization.
Typical PSV ISA symbol:
Note: #### place holder for the instrument tag number and actual set pressure.

## Slide 5: PSV Program Requirements
All pressure retaining vessels over 15PSIG are REQUIRED to have PSV protection per ASME Code & Standards.
All large low pressure storage tanks should have over and under pressure protection.
  Typically governed by either the state, industry or facility’s insurer.
All PSV’s utilized in process facilities are governed under one of two ASME Codes:
  ASME Section I
    Fired vessels
  ASME Section VIII
    Unfired vessels
All PSV’s utilized in a process plant are REQUIRED to have a defined inspection, maintenance and calibration program executed by an ASME certified provider.

## Slide 6: PSV

## Slide 7: PSV

## Slide 8: Rupture Disc’s
Related type of pressure safety device.
A rupture disc is typically a metal diaphragm designed to rupture (break) at a specific pressure and temperature.
Commonly utilized in conjunction with a PSV.
Utilized most often on processed that can not tolerate any incidental leakage.
  e.g. Extremely toxic or corrosive fluids.
Rupture discs help prevent incidental leakage by providing a primary seal between the fluid and the environment.
Rupture discs enhance PSV reliability by protecting the PSV from corrosive fluids.
Single use device.

## Slide 9: Pressure/Vacuum Reliefs
Protect vessels from both over and under pressure events.
Typically utilized on large low pressure storage tanks.
Low pressures and low vacuum conditions.
  Typically set pressures:
    Overpressure: <2PSI,
    Vacuum: <-2PSI
    Not uncommon to have setpoints of +/- 2 inches of water column (WC).

## Slide 10: Pressure/Vacuum Reliefs

## Slide 11: Pressure/Vacuum Reliefs

## Slide 12: Bad things happens when PSV’s Fail

## Slide 13: Relief Valve References
https://www.youtube.com/watch?v=w34XD71DqfQ
https://www.youtube.com/watch?v=YA3XUEIcXA0
https://youtu.be/0N17tEW_WEU

## Slide 14: Isolation (block) Valves
What is there primary purpose?
  Allow or prevent flow.
    Isolate one part of the process from another.
  Two position: Open or Closed
  Valves are designed and expected to shutoff completely. (Zero Leakage)
    AKA: “Bubble Tight”
  Very common for plant personal to be working downstream of the isolation valve.
    Requires provisions for “Lock Out/Tag Out” (LOTO).
  For personal safety may be used in a “double block” or “double block & bleed” arrangement.
  Have very limited throttling capability.

## Slide 15: Isolation (block) Valves

## Slide 16: Manual Valves
Multiple types
Some of the various types:
  Globe Valve Knife Gate Valves
  Gate Valves Pinch/Boot Valves
  Ball Valves Needle Valves
  Butterfly Valves
Typically actuated with a Lever, Handwheel, Gear Box with Handwheel or Chain-wheel.
Typically have some method to lock in a position (LOTO).

## Slide 17: Manual Valve ISA Symbology

## Slide 18: Manual Valve Examples

## Slide 19: Manual Valve Examples

## Slide 20: Automated Isolation Valves
The valves themselves are generally the same as manual isolation valves with the exception of adding some form of actuation so they can be controlled remotely.
Most common actuation types are:
  Pneumatic (air operated valve or “AOV”)
  Electric Motor (motor operated valve or “MOV”)
  Electric Solenoid (solenoid operated valve or “SOV”)
Will usually have a position feed back signal so remote operator has indication of position and proper functioning.

## Slide 21: Automated Isolation Valves

## Slide 23: AOV, MOV, SOV Valve Symbols
Symbol dissection
  “HV” = Hand Valve
  #### = place holder for the instrument or loop number
  “X” = place holder for actuation method
    “A” Air operated
    “M” Motor operated
    “S” Solenoid operated

## Slide 24: Control Valves
Control valve are valves specifically designed to THROTTLE.
  That is; the valve will be constantly adjusting the valve’s orifice (port); varying the flow rate of a process fluid based on a command from the control system/operator.
They not generally expected to provide complete shutoff when closed.
  Not “Bubble” Tight:
Most common actuation is Pneumatic.
Generally have a “fail” position upon loss of control signal.
  Fail Closed, Fail Open, Fail Last Position (locked)
Control valve assemblies are composed of three components:
  Valve body
  Actuator
  Positioner

## Slide 25: Nomenclature: Control Valve Assembly Components

## Slide 26: Control Valve Types
Most common control valve types
  Globe (Sliding Stem)
  V-notch Ball (Rotary)
  Hi-Performance BFV (Rotary)

## Slide 27: Control Valve ISA Symbols
“x” = Place holder for function:
  e.g., F = Flow, L = Level,
  T = Temperature, P = Pressure, etc.
### = Place holder for loop or instrument tag number
“y” = Place holder for valve fail condition
  e.g., C = Closed, O = Open,
  L = Lock or Last Position

## Slide 28: Other Types of Valves
Check Valve
  Valve designed to only allow flow in one direction
    Commonly used on the outlet of a pump or compressor to prevent reverse flow through the pump (reverse rotation/back spin)

## Slide 29: Other Types of Valves
Stop Check Valve
  Under normal operation operates the same as a check valve, but has a method to lock the valve closed.
    Used on the steam outlet on boilers.

## Slide 30: Other Types of Valves
Three Way Valves
  Valve with 3 ports
    Ball or globe style valves
  Used for converging (mixing) flow
    Two inlet flows, one combined outlet flow
      E.g.: Temperature control
  Used for flow splitting/switching
    Single inlet, flow is divided between two outlets
    Can be throttling or on/off

## Slide 31: Other Types of Valves
Blowdown Valves
  Specific valve used on boiler mud drums to remove contaminates from boiler feed water.
    Manual or automatic
“MAXON” Valves
  MAXON is a trade name commonly used to refer to the double block & bleed valves used on the natural gas supply to a boiler or burner.
    Required under NFPA 85B Code

## Slide 32: Other Types of Valves
All kinds of “Special” Service Valves e.g.:
  Cryogenic
  Steam Conditioning
  Attemperator Valves
  Steam Traced Valves
  Dehydration Valves
  Etc.

## Slide 33: Valve Operational Concerns
Leakage:
  Internal: Fluid leaks from the upstream side to the downstream.
    Prevents proper safety for maintenance procedures.
      Always completely open drains to insure complete closure and safe operations.
    May contaminate downstream process creating safety or quality issues.
    Leakage will continue to worsen unless addressed.
  External: Fluid leaks to the environment.
    SEH issues and potential fines.
      Any observed or suspected external leakage must be reported to the Leak Detection and Remediation (LDAR) or maintenance team for resolution.
      PSV’s may exhibit “weeping” (small traces of product leaking to the vent) this is an indication there is foreign material trapped between the disc & seat, damage to the disc & seat or possibly that the PSV setpoint is to close to the process normal operating pressure.
        Requires immediate investigation & remediation.

## Slide 34: Valve Operational Concerns
Sticking
  Isolation valves left in one position for long periods of time can & will get stuck.
    Especially prevalent in hot, dirty or heavy viscous applications, but can happen anywhere.
    It is highly recommended that there be a program to “exercise” isolation valves regularly.
      Routinely completely or partially stroke the valve to help insure they are working properly.
  Control valves can become “gummed up” resulting in stiction.
    Stiction in control valve will result in operation issues and potentially lose of control
      May result in SEH, quality or production issues.

## Slide 35: Valve Operational Concerns
Wear & Tear
  Automated isolation and control valves are highly subject to wear & tear under normal operation.
    This may show up as various symptoms, e.g., stiction, backlash, sloppy control, product quality issues, etc.
  Operators should be watching for these symptoms and inspecting valves on a regular basis.
    Regular visual inspections;
      Looking for leaks, jerky or erratic movement, stroke times changing, etc.
    Diagnostics
      Many automated and control valve come with onboard diagnostics to alert operations and maintenance of performance issues. ------USE THEM -----
    Bump tests
      When SAFE; occasional small changes to the valve input to observe the valve response.