## Slide 1: P&ID Nomenclature & symbology
Development of a 21st Century Industrial Process Operations Program is supported by the National Science Foundation under Grant No. 1700558. Any opinions, findings, and conclusions or recommendations expressed on this site are those of the authors and do not necessarily reflect the views of the National Science Foundation.

## Slide 2: ANSI/isa s5.1-2009
The symbology and nomenclature utilized on P&ID’s generally governed by ANSI/ISA S5.1-2009 standard
  The standard provides a highly recommended means of showing a process plant’s instrumentation and basic control functions in a commonly understood manner.
  It covers the bulk of instrument and control symbols along with a recommended nomenclature for process instrumentation depicted on P&ID’s

## Slide 3: ANSI/isa s5.1-2009
NOTE:
The standard is not an absolute
    Facilities will apply modifications, alternative symbols, and nomenclature to meet their specific requirements.
It is a best practice and HIGHLY recommended that every P&ID package include a symbol and nomenclature “legend”.
    This consists of the first sheet(s) of the P&ID package documenting all the symbols and nomenclature utilized in the P&ID’s

## Slide 4: ANSI/isa s5.1-2009
Latest version and publication
  18 September 2009
  Available from the ISA publications bookstore
It’s about 128 pages for your reading enjoyment
Reference for this class:
  Fundamentals of Process Control Theory
    Third Edition
    Paul W. Murrill
    Appendix A
Handouts

## Slide 5: Instrument tagging & nomenclature
An instrument tag usually consists of 3 elements
  AAAA – BBBB – CCCC
    AAAA Unit or Area Designator
    BBBB Loop/Instrument Function
    CCCC Loop/Instrument Number
      Some facilities will add a fourth element, that being a system (subsystem) identifier to the tag

## Slide 6: Instrument tagging & nomenclature
The first element (AAAA) is the unit, plant area or equipment area
  e.g.:
    038- might designate the 38 unit
    07- might designate the #7 boiler
    07NG- might designate the #7 boiler, natural gas system
    944- might designate #9 machine, area 44 of that machine
  This designator’s scheme and meaning is completely up to the owner.
    Often for clarity and to save space on the P&ID the first element is located on the “sheet” level in the sheet title box.

## Slide 7: Instrument tagging & nomenclature
The second element (BBBB) is the loop function.
This is a combination of letters depicting the instrument or loop function.
  Ref: Murrill; Appendix A, Page 269
  Ref: Handout (Part of ISA S5.1-2009)

## Slide 8: Instrument tagging & nomenclature
- PI
  First letter = Variable ∴ P = Pressure
    There is no modifier
  Next letter = Read out ∴ I = Indicate
- PDI
  First letter = Variable ∴ P = Pressure
  Next letter is a Modifier ∴ D = Differential
  Next letter = Read out ∴ I = Indicate
- TIC
  First letter = Variable ∴ T = Temperature
    There is no modifier
  Next letter = Read out ∴ I = Indicate
  Next letter = Output function ∴ = Control
- TDIC
  First letter = Variable ∴ T = Temperature
  Next letter is a Modifier ∴ D = Differential
  Next letter = Read out ∴ I = Indicate
  Next letter = Output function ∴ C = Control

## Slide 9: Instrument tagging & nomenclature
The second element (cont.)
  - LIC
    First letter = Variable ∴ L = Level
      There is no modifier
    Next letter = Read out ∴ I = Indicate
    Next letter = Output function ∴ = Control
  - LV
    First letter = Variable ∴ L = Level
    Next letter = Output function ∴ V = Valve
      Sometimes designated as LCV ∴ Level Control Valve

## Slide 10: Instrument tagging & nomenclature
The second element (cont.)
A couple of fun ones:
  LAH
  PAHH
  ZSC
  ZSO
  PSV
  LSL

## Slide 11: Instrument tagging & nomenclature
The second element (cont.)
First letters : -C, -D, -G, etc. are users choice.
The meaning must be documented by the owner.
  e.g.:
    - C in a paper mill is normally “consistency”
      A measure of the amount of pulp fiber in a specified amount of water
    - C in a power plant is normally “conductivity”
      A measure of water purity

## Slide 12: Instrument tagging & nomenclature
The third element CCCC is the instrument/loop number
It is normally a numerical instrument/loop identifier (e.g., -1023)
  May include alpha characters

## Slide 13: Instrument tagging & nomenclature
Define the following:
  016-PV-0256
  4-CIC-001
  655-AIR-958
  18-LSL-0001
  18-LSH-0002
  36-PSV-204
  PM1-TCV-256A
  PM1-TCV-256B

## Slide 14: Instrument tagging & nomenclature
Occasionally you will see instruments numbers like:
  84-LV-256A, 84-LV-256B
  The letter at the end of the instrument number indicates both of these instruments are part of loop #256
    Two valves: An “A” and “B” valve controlled by the same controller
  036-PICA-1235, 036-PICB-1235
    Two control loops utilizing the same input signal
      Two different control ranges or strategies
      Maybe controlling two output devices

## Slide 15: P&ID instrument & signal symbols
Process lines, sensing lines, pneumatic or electronic signals are typically shown as solid or dashed lines.
Instrument and control symbols consist of a series or combination of circles (bubbles), squares, diamonds, hexagons
  These may have dashed or solid lines inside the symbol denoting location.

## Slide 16: P&ID Process & Signal Symbols
Process Line
Process Line with Secondary Connecting Line
Instrument Signal Lines

## Slide 17: P&ID instrument & control symbols
Circles (bubbles)
  Individual instruments, controllers or device identifier
Square
  Shared display
Diamond
  Logic or safety function
Hexagon
  Computer function
    Calculation, totalize, average, etc.

## Slide 18: P&ID field device symbols
Generic Individual Field Mounted Device
Individual Field Mounted Local Indicator
Individual Field Mounted Indicator & Electronic Transmitter

## Slide 19: P&ID field device symbols - Sensors
What do you think this means?
TW with TE and TT
Bubbles touching
All mounted in a single housing or assembly
TW with TE and TIT
2 Bubbles touching 1 not
TW & TE mounted in a single housing xmitter remote mounted in the field
TW with TE and TIT
2 Bubbles touching 1 not
TW & TE mounted in a single housing xmitter remote mounted in a panel

## Slide 20: P&ID field device symbols - Valves
Generic Valve Symbol
Manually operated
Not normally used during operations
  Unit shutdown & Isolation
  Equipment block & bypass
Normally Open
Normally Closed

## Slide 21: P&ID field device symbols - Valves
Other Valve Symbols (Less Common)
Angle Valve
Butterfly Valve or Damper
Three Way Valve

## Slide 22: P&ID field device symbols - Valves
Manual Valve Symbol
Manually operated
Operator adjustable during normal operations
  Throttling Service
Normally shown “open”

## Slide 23: P&ID field device symbols - Valves
Automatic Valve Symbols
Spring and Diaphragm, Air Operated Control Valve
Most common control valve actuator construction
Has an inherent fail position on loss of air noted below symbol or “up/down” arrow
  FC = Fail Closed
  FO = Fail Open
  FL = Fail Locked or “in Place”

## Slide 24: P&ID field device symbols - Valves
Other Automatic (Powered) Valve Symbols
Basic Symbol
When shown as above: assumed to be pneumatic cylinder actuator
Solenoid Valve
Motor Operated Valve
  Older plants will show the actuator as a bubble with a “M”
Correct pneumatic cylinder actuator symbol

## Slide 25: P&ID field device symbols – MISC. Valves
Check Valve
Stop Check Valve
Safety Relief (overpressure)
How would you show a safety relief valve for underpressure?