## Slide 1: Control Valves
Development of a 21st Century Industrial Process Operations Program is supported by the National Science Foundation under Grant No. 1700558. Any opinions, findings, and conclusions or recommendations expressed on this site are those of the authors and do not necessarily reflect the views of the National Science Foundation.

## Slide 2: Learning Objectives
Understand the purpose, types, and construction of control valves, actuators and positioners
Understand the basics and importance of proper control valve selection, sizing and application
Gain an understanding of the required engineering to properly size, engineer, and select a control valve assembly

## Slide 3: Purpose of a Control Valve?
First ask yourself:
  What is a Control Loop?
A Control Loop is:
  A system of sensors, controllers and final control element (typically a control valve) whose purpose is to maintain a given process variable within a required operating range.
  To remove or minimize process variability induced from any number of disturbances
Sad Side Note:
  ~60% of control loops fail to perform their primary function!

## Slide 4: Purpose of a Control Valve?
The Control Valve
  A subsystem of a Control Loop that provides the “muscle” to manipulate a given process fluid flow to compensate for the load disturbances.
  A major contributor to control loops failing to perform their primary function:
    Control valve issues
      e.g., incorrect sizing, selection, lack (no) of maintenance, etc.

## Slide 5: Nomenclature: Control Valve Assembly

## Slide 6: Basic Control Valve Types – First Segregation
Sliding Stem Rotary

## Slide 7: General Purpose (Utility) Sliding Stem

## Slide 8: Heavy Duty Sliding Stem

## Slide 9: Special Service Valves

## Slide 10: Eccentric Disc (E-disc)

## Slide 11: E-Plug

## Slide 12: Segmented V-Ball Valves Trunnion Mounted

## Slide 13: Special Application Rotary Valves

## Slide 14: Why? Sliding stem vs. Rotary
Sliding Stem
Pressure Class
  ANSI 150-4500#
Temperature
  Cryo-1000+F
Valve characteristic
  Trim characterized
Pressure Drop
  Typically full ANSI Class
“Clean” Fluids
Rotary
Pressure Class
  Norm ANSI 150-600#
    Above 600# special
Temperature
  Norm -20-500F max
    Below -20 and above 500F special
Valve Characteristic
  Fixed by design
Pressure Drop
  Limited by design, size and temp
Clean to Slurry

## Slide 15: Pressure Class vs. Max Pressure Drop
Pressure class defined by ASME for pressure containment.
Determined by body material, process temperature and pressure.
Max pressure drop determined by manufacturer based on valve design, materials and process temperature
Ref: CVHB pages 76-83

## Slide 16: OOPS!

## Slide 17: What is Valve Trim?
It’s NOT fancy leather and chrome to make the valve look pretty!!!!!!!!!

## Slide 18: INHERENT Characteristic
The valve flow characteristic is the relationship between the flow rate through the valve and the valve travel as it is varied from 0-100%
The Inherent flow characteristic refers to the characteristic observed with a constant DP across the valve
The Installed flow characteristic means the one obtained in services where the DP varies with flow and other process changes in the system

## Slide 19: Inherent Valve Characteristic

## Slide 20: INHERENT Characteristic Definitions
Linear
  Flow rate is directly proportional to the valve travel
  Valve gain is constant throughout valve travel
  Typically level and some flow applications
Equal Percent
  Equal increments of valve travel produce equal percentage changes in the existing flow
  Valve gain increases with increasing valve travel
  Most common characteristic used
Quick Open
  Provided for maximum change in flow rate at low valve travel, shapely reduced changes in flow at increased valve travel
  Valve gain decreases with increasing valve travel
  Mostly on-off

## Slide 21: Inherent Valve Characteristic
In rotary type valves it is generally fixed
  V-ball Equal-Percent
  E-disc and e-plug ~Linear
In Sliding stem can be changed via trim design
  Cage characterized
  Plug Characterized

## Slide 22: Control Valve Shutoff
ANSI/FCI 70-2-1991
Industry standard for seat leakage of new control valves tested at the factory under specific conditions
Classes range from Class I to VI
  Ref: CVHB Page 92 & 93
MOST OVER SPECIFIED VALVE REQUIREMENT!!!!!!!!!
COST for high class shutoff requirements increase rapidly as size, pressure and temp increase.

## Slide 23: Control Valve Shutoff

## Slide 24: Control Valve Actuation
Functions of the actuator
  Provide positioning of the valve plug relative to the seat
    Control the variable orifice area
    Maintain the plug stability
  Provide fail mode
    i.e. Fail closed, Fail open, Fail last position
  Provide seating forces to achieve shutoff
Most common actuators are pneumatic spring and diaphragm or piston

## Slide 25: Spring and Diaphragm Actuator

## Slide 26: Piston Actuators
Typically double acting
  Pneumatic signal dives actuator in both directions
  Sometimes my include a spring
    Caution: a spring in a piston operator does not necessarily mean it has a fail mode (bias spring)

## Slide 27: S&D vs. Piston
S & D
  Most Common
  Simple Design
  Inherent Fail Action
  Very Reliable
  Limited Stroke Length
  Limited Maximum Force
Piston
  High pressure capable
  Highest thrust to size
  Long Stroke Available
  Fail Action
    Special Spring Constructions
    Trip Valve & Volume Tanks

## Slide 28: Actuator Sizing
Sliding Stem
  Pressure Drop
  Unbalance Area
  Seat Load
    Shutoff Class
  Packing Friction
Rotary
  Breakout Torque
    Valve Type, Seal Design, Bearings & DP
  Dynamic Torque
    Valve Type & DP effective

## Slide 29: The Positioner
Three Types
  Pneumatic
  Electro-pneumatic
  Digital
Provides mechanical feedback to ensure accurate control.
  Increases reliability
  Increases dependability
  Increases wear life

## Slide 30: Why do we size control valves?
Economics
Controllability
The right valve for the best performance.

## Slide 31: Agenda
Liquid Sizing
Gas Sizing

## Slide 32: Pressure/Velocity Profile

## Slide 33: Flow Coefficient - Cv

## Slide 34: Basic Liquid Flow Equation

## Slide 35
P
G
Q
Water
Flow
Slope = Cv
Q = Cv
P
G
Basic Curve

## Slide 36: Choked Flow
P
Allowable
Q
Water
Flow
P
G
(“choked flow”)

## Slide 37: Other Sizing Influences
Piping Geometry
Fluid Properties
Mixed Phase
Solids
Others

## Slide 38: Agenda
Liquid Sizing
Gas Sizing

## Slide 42: Critical Flow (Choked Flow)
Occurs when gas reaches sonic velocity at the vena contracta.
An increase in P by decreasing P2 will not increase the flow, as in liquids.
An increase in P by decreasing P2 will increase the noise.

## Slide 43: Other Sizing Influences
Piping Geometry
Fluid Properties
Mixed Phase
Solids
Others

## Slide 44: Operator Valve Considerations
Cavitation
Flashing
Erosion
Corrosion
Noise
Performance

## Slide 45: Pressure/Velocity Profile

## Slide 46: Cavitation - Pvc vs. Pv

## Slide 47: Cavitation Damage

## Slide 48: Cavitation Damage

## Slide 49: Cavitation Damage
When choked flow causes cavitation (as opposed to flashing) the following happen:
  Noise
  Damage
  Vibration
Cavitation damage is a function of
  Intensity
  Materials of construction
  Time of exposure
  Quantity of flow
  Valve/Trim design
  Leakage while closed

## Slide 50: Flashing
If the valve outlet pressure remains below the vapor pressure of the liquid, the bubbles will remain in the fluid and the process is said to have flashed.
Flashing is defined by the liquid vapor pressure and the process downstream pressure and is not something we can prevent.

## Slide 51: Flashing
Pv is a function of temperature.
If Pvc < Pv AND P2 < Pv, then flashing.
P1
P2
P2
P1
Pv
P
vc

## Slide 52: Flashing Damage

## Slide 53: Flashing Damage
When flashing occurs the following happen:
  Damage
Flashing damage is a function of
  Intensity
  Materials of construction
  Time of exposure
  Quantity of flow
  Valve/Trim design
  Leakage while closed

## Slide 54: Erosion
The removal of valve component material by the impingement of high velocity particles on the valve component(s).
Often accelerated by the materials being “weakened” by corrosion.

## Slide 55: Erosion

## Slide 56: Erosion - Consequences

## Slide 57: Erosion

## Slide 58: Erosion - Corrosion
Notes: A similar situation in a CP body. You can see the “scoops” of metal removed that match up with the pattern of the seat ring retainer.

## Slide 59: Erosion Damage
When erosion occurs the following happen:
  Damage
Erosion damage is a function of
  Intensity
    Velocity, Hardness of particles, Quantity of particles.
  Materials of construction
  Time of exposure
  Quantity of flow
  Valve/Trim design

## Slide 60: Control Valve Noise
Control Valves are typically sized for < 85 dBA. An SPL above 110 dBA* is not recommended since high vibration levels can result, which can lead to severe damage to the valve, actuator, instrumentation, and downstream piping.
Based on calculation with STD schedule pipe

## Slide 61: Typical Sound Pressure Levels
  Quiet Residence - 50 dBA
  Conversation - 60 dBA
  Vacuum cleaner @ 10 ft - 70 dBA
  Heavy Street Traffic - 90 dBA
  Jack Hammer - 100 dBA
  Jet Airplane @ 200 ft - 120 dBA
  Threshold of Pain - 140 dBA

## Slide 62: Noise Treatment Methods
1.) Source Methods
  Reduce actual amount of acoustic energy present.
2.) Path Methods
  “Masking” methods (i.e. insulation, pipe wall thickness, etc…)
  Do not use when excessive vibration is expected.
Notes: The “Acoustic efficiency approach” simply means that the design is developed such that the acoustic efficiency factor is reduced in one manner or another.
The “Frequency shifting approach” means that, rather than concentrating upon reducing the internal sound pressure level, the frequency is shifted into a range where the human ear is less sensitive to the noise and less energy is transferred to the pipe.

## Slide 63: Operator Valve Considerations
Wear & Tear
Poor Performance
  Stiction
  Backlash
  Sluggish
Air Supply Issues
  Leaks
  Dirt
  Moisture
  Low Pressure
Leaks
  Internal
  External