## Slide 1: Process Operations Tech II
Development of a 21st Century Industrial Process Operations Program is supported by the National Science Foundation under Grant No. 1700558. Any opinions, findings, and conclusions or recommendations expressed on this site are those of the authors and do not necessarily reflect the views of the National Science Foundation.

## Slide 2: Course Objectives
Instrumentation
  Measurement transmitters
  Final control elements
Process Industry Documentation
  Process Flow Diagrams (PFD’s)
  Piping & Instrument Diagrams (P&ID’s)
  Logic Diagrams
  Electrical Schematics
  Hydraulic Schematics

## Slide 3: Referenced Sources
Fundamentals of Process Control
  Murrill
ANSI/ISA-S5.1
  International Society for Automation
Measurement & Control Basics
  Hughes
Control Loop Foundation- Batch & Continuous Processes
  Blevins & Nixon
The Control of Boilers
  Dukelow
Flow Measurement Engineering Handbook
  Miller
Process Instruments & Controls
  Lipták

## Slide 4: Measurement Concepts What is a Transmitter?
A device that senses a specific attribute or property of a process and creates a signal that can be transmitted to a remote location.
A field device consisting of a housing, electronics and sensing element used to transmit various information to the operators via the control system.
The transmitter produces an output signal value that has a predetermined relationship to the sensed attribute or variable, the input signal.

## Slide 5: Measurement Concepts Transmitter Output Signals
Analog
  Pneumatic
    3-15/3-24/6-30PSI
  Electronic
    4-20MADC
    4-20MADC HART
Digital
  FieldBus
  WirelessHART

## Slide 6: Did you notice anything about the analog output signals???
Why doesn’t the analog process signal start @ zero?
  Live zero

## Slide 7: Measurement Concepts Transmitter Terminology
Zero
  The process measurement point which corresponds to the transmitter minimum output
    0PSI=4MADC, 100F=4MADC
Span
  The difference between the maximum and minimum output signals of a transmitter
    4-20MADC=16MA Span
  The difference between the maximum and minimum process measurement values
    100-550F=450F Span

## Slide 8: Measurement Concepts Transmitter Terminology
The accuracy of a measurement refers to the closeness with which the measurement approaches the true value of the variable being measured.
  Accuracy Specs
    +/-X% of span or full scale
    +/-X% of reading
Repeatability is the closeness of agreement among a number of consecutive measurements of the output for the same value of the input
  In today's world interchangeable with reproducibility

## Slide 9: Measurement Concepts Transmitter Terminology
The sensitivity of a measuring device is defined by the ratio of the output signal change to the change in the measured variable. Sensitivity has the engineering units of the output signal divided by the engineering units of the input signal.
True, But…….
In the real world we use the inverse, typically referred to as resolution.
The input span divided by output span
  550-100F = 450F span/20-4MADC = 16MA span
  28.125F/MA

## Slide 10: Types of Process Measurements
Three types:
  Physical
  Analytical
  Inferred/Calculated

## Slide 11: Physical
Physical properties of the process fluid which can be relatively directly measured.
Examples:
  Pressure
  Temperature
  Level
  Flow
  Position
  Acceleration

## Slide 12: Measurements Pressure
What is Pressure?
Pressure is defined as force per unit area
  PSI(G)
  PSIA
  Vacuum (inches of H2O, mm of HG)
  HEAD (inches of H2O, Feet H2O)
Liquid Measurement
  Always fast
  Always noisy
Gas or Vapor Measurement
  Can be fast or slow
  Normally not noisy

## Slide 13: Measurements Temperature
What is Temperature?
Temperature is a common arbitrary scale/reference to describe the amount of heat an “object” contains.
  Degrees F, C
Temperature is always slow to very slow
May contain “deadtime”
  The interval of time between the initiation of a some kind of change and the start of the resulting observable response
Thermowells required for protection of element.
  They slow the measurement response time of the xmitter and can add additional deadtime.

## Slide 14: Measurements Temperature
TC’s
  Heating the junction of two dissimilar metals causes a contiguous emf (microvolt’s) to be generated
    This can be measured then be compared to a reference
  Signal is always non-linear
  A good quality installation is required for good measurement
    Every junction in the wiring can cause this emf
  There are multiple metal combinations available for various application
    Type’s J,T,K,E most common

## Slide 15: Measurements Temperature
RTD’s
  Increasing temperature increases a metals resistance
  A very pure, fine wire wrapped around a mandrel then sealed
  Linear
  Most common is Platinum(100 Ohm)
    General industrial use
  Power generation will also use Copper(10 Ohm)
    Very large motors and most generators.

## Slide 16: Measurements Level
What is level?
A measurement of the height of a product in a vessel
  Inches, Feet, Percent
Two Position Level
  Floats with switches
    High and low measurement
Continuous Level Measurement
  Head
  Displacement
  Ultrasonic
  Radar
  Others

## Slide 17: Measurements Flow
What is Flow?
The amount (volumetric or mass) of product passing a specific point in a specific period of time.
  GPM, M/HR, PPH
Flow measurement has extensive selection of technologies
  They all have their +&-’s
  Selecting the most effective flow meter involves many considerations
    Liquid, Gas or Vapor?, Viscous?, Reynolds Num?, Clean or Dirty?, Slurry?, Pressure, Temp, Required range of measurement, Cost, Piping, Accuracy required?

## Slide 18: Measurements Flow
Some of the most common technologies:
  Differential(DP)
  Magnetic(Mag Flow)
  Vortex
  Mass
Flowmeters have specific installation requirements: e.g. should always be installed upstream of major flow disruption, Control Valves, pipe elbow, pipe tee’s

## Slide 19: Measurements Position
What is Position?
Location
Discrete
  Switches
    Open or closed
Continuous Position Measurement
  Hall Effect
  LVDT
  RVDT

## Slide 20: Measurements Acceleration
What is acceleration?
A measurement of the amount of energy is being put into a component or how much is being generated by a component
  “g’s”
Commonly utilized for monitoring & control on vibratory equipment
Used extensively for vibration monitoring
Piezo Electric Crystals
  Accelerometers

## Slide 21: Analytical Measurements
Generally can not be measured directly.
These process properties requires complex technologies to measure.
Can or should be considered online lab testing
These properties very often relate to Environmental requirements/regulations, Product Quality or Reliability requirements for the process operation

## Slide 22: Some Analytical Measurements
pH | H2S | CO2 | Excess O2
Density/SG | CO | Opacity | SO2
Conductivity | Humidity | Combustibles | NOx
HC | Consistency | Freeness | Brightness
Si | Turbidity | Dissolved O2 | CL
CLO2 | O3 | Moisture | IR
ORP | Color | CEMs | % Solids
Calorie/BTU | TOD | Total Sulfur | Ash
Corrosion | Hg | % H2O | N2
Refraction | TOC | Viscosity | Dioxin

## Slide 23: Inferred/Calculated
Kappa
Pour Point
Pen Percent
HPT/D
BTU
Torque
Shear
Viscosity

## Slide 24: Assignment
Research Project