## Slide 1: Piping and Instrument Drawing

## Slide 2: Piping and Instrument Drawing
Identify the names and content of typical Instrumentation & Control Systems documents.
Identify the key components of P&IDs.
Recognize basic ANSI/ISA-5.1-2009 ID and symbolism methods.
Recognize common measurement notations.
Read / interpret tag and control loop numbers.

## Slide 3: What is a P&ID Diagram? (Piping & Instrumentation Diagram)
https://www.youtube.com/watch?v=lBJnU1MJAts
https://www.youtube.com/watch?v=3CYTe7AvRvM
https://www.youtube.com/watch?v=kujHQgK352o

## Slide 4: Instrumentation & Control Documentation
Instrumentation & control systems require documentation for design, procurement, installation and maintenance.
Typical documentation includes:
  Instrumentation Index
  General Specifications
  Installation Detail Drawings
  Location Drawings
  Piping and Instrumentation Drawings (P&IDs)

## Slide 5: Instrumentation & Control Documentation
Instrumentation Index: Lists instruments used by tag number.
General Specifications: Contain applicable codes, standards, wiring and cable requirements, ventilation requirements, power supply requirements, etc.
Installation Detail Drawings: Provide information and requirements for proper mounting and connections of a specific instrument.

## Slide 6: Instrumentation & Control Documentation
Location Drawings: Identify where an instrument is to be installed.
Piping and Instrument Drawings: Detailed schematic drawings of equipment, piping, and instrumentation on a project. The schematic symbols used are governed by national and international standards (ANSI/ISA)

## Slide 7: Piping and Instrument Drawing (P&ID)
Detailed, schematic drawing of equipment, piping, and instrumentation on a project.
Uses a common language of schematic symbols to describe components in an instrumentation & control system.
Typically Includes:
  Instrumentation
  Valves
  Mechanical Equipment
  Flow Directions
  Control Inputs, Outputs and Interlocks
  Pipe Connections, Sample Lines, and other Fittings

## Slide 8: How to Read a P&ID? (Piping & Instrumentation Diagram)
https://www.youtube.com/watch?v=j4EOTerfyTY

## Slide 9: ANSI/ISA-5.1-2009: ID and Symbolism Methods
Discrete instruments and their functions.
Shared display and control functions.
Distributed control functions.
Computer control functions.
Programmable logic controller display and control functions.
Application software display and control functions.

## Slide 10: ANSI/ISA-5.1-2009: Additional Content
Definitions of terms used in instrumentation documentation
Identification Letters for the Instrument and Function Identification System
Graphic Symbol Tables
  Instrumentation Device and Function Symbols
  Measurement Symbols and Notations
  Line Symbols
  Final Control Element Symbols
  Control Valve Failure and De-energized Position Indications
  Functional Diagramming Symbols
  Signal Processing and Function Block Symbols
  Binary Logic Symbols
  Electrical Schematic Symbols
Graphic Symbol Dimension Tables

## Slide 11: ANSI/ISA-5.1-2009: Annexes
A – Identification System Guidelines
B – Graphic Symbol Guidelines

## Slide 12: Instrumentation Device and Function Symbols

## Slide 13: Instrument Symbols (NCCER)

## Slide 14: Measurement Symbols
3.1.48 primary element: an external or internal instrument or system element that quantitatively converts the measured variable into a form suitable for measurement; see also detector and sensor:

## Slide 15: Line Symbols

## Slide 16: Drawing Lines (NCCER)

## Slide 17: Final Control Element Symbols

## Slide 18: Final Control Element Actuator Symbols

## Slide 19: Control Valve Failure and De-energized Position Indications

## Slide 20: Graphic Symbols (NCCER)

## Slide 21: Graphic Symbols (NCCER)

## Slide 22: Measurement Symbols: Notations

## Slide 23: Tag Numbers (NCCER)
A tag number can identify instrument location, function, and its related instrument loop. Area designation numbers identify location when the process is spread across multiple buildings or areas.

## Slide 24: Tag Numbers – First Letter (NCCER)

## Slide 25: Tag Numbers – Succeeding Letters (NCCER)
In a tag number with two letters, the second letter usually designates the instrument function.
When there are more than two letters, the third letter may modify the first letter or identify a secondary function.

## Slide 26: Tag Numbers – Loop Identification (NCCER)
When similar instruments are used in a loop, such as these two flow transmitters, a suffix letter is added to distinguish them.

## Slide 27: Control Loops (NCCER)
A number of control loops are required for most processes.
Control Loop Numbers are therefore assigned on P&IDs to identify specific control loops.

## Slide 28: Control Loop Identification (NCCER)
Control Loop Number

## Slide 29: P&ID Example: Temperature Control Loop
Steam
Kettle Reboiler / Heat Exchanger
Temperature
Transmitter
Temperature
Indicator
Temperature Controller
And Recorder
Pneumatic
Control
Valve

## Slide 30
Discrete
Field Mounted
Visible at operator location
Normally accessible
Control Valve
Actuator
Steam
Kettle Reboiler / Heat Exchanger
Temperature
Transmitter
Temperature
Indicator
Temperature Controller
And Recorder
Pneumatic
Control
Valve

## Slide 31
Tag Numbers: ID type and function of device
1st Letter: Measured Variable
  T – Temperature
  F - Flow
2nd & 3rd Letters: Designate function or modify meaning of first letter.
  T – Transmitter
  I - Indicator
  RC – Recorder/Controller
  CV – Controller, Valve
Control Loop Number

## Slide 32
Pneumatic Signal
Piping
Filled thermal element capillary tube.
Filled sensing line between pressure seal and instrument
Temperature Control Valve
(Pneumatic)
U-Tube Heat Exchanger /
Kettle Reboiler

## Slide 33: DISCLAIMER & USAGE
  This material is based upon work supported by the National Science Foundation's Advanced Technological Education Program under Grant No. 1801177.
  Any opinions, findings, and conclusions or recommendations expressed in this material are those of the author(s) and do not necessarily reflect the views of the National Science Foundation.
33