## Slide 1
ACADs (08-006) Covered
Keywords
Living organisms, mixed bed, resin, degassing, organic material,
Description
Supporting Material
4.20.1.13c | 4.20.1.13d | 4.22.1.1 | 4.22.1.6
4.22.1.7 | 4.25.7 | 4.30.3 | 
Notes: <number>

## Slide 2: CHEMISTRY AND RADCON CR-2 PLANT CHEMISTRY CONTROL
Ivelisse Ortiz-Hernandez, PhD.
<number>

## Slide 3: OBJECTIVE
The student successfully completing this lesson will be able to describe the mechanisms and purposes of chemistry control in the primary and secondary plants.
<number>

## Slide 4: Overview
The specific corrosion control methods applied to the RCS and Secondary Systems will be discussed.
The components of primary interest are the fuel clad and the Steam Generator U-tubes.
Fuel cladding - A protective or insulating layer fixed to the outside of a building or another structure.
The Steam Generator U-tubes must be protected to prevent the release of radioactive material normally present in the RCS to the secondary plant.
<number>

## Slide 5: Overview
The clad must be protected from severe corrosion because it is the primary boundary against release of radioactive fission products from the fuel to the RCS.
Releasing fission products to the RCS will cause a large increase in plant radiation levels, increase the problems associated with disposal/handling of RCS water, and may pose a threat to the public during severe casualty conditions.
<number>

## Slide 6: Overview
Plant cooling systems must be protected from organic invasion.
Chemical biocide treatment is necessary to preclude complications due to organic growth.
<number>

## Slide 7: Radiation Effects in the Primary System
Basic Definitions
  Neutron flux – flow of neutrons through an area as a function of time.
  Gamma rays - possess no charge or mass; thus emission of Gamma rays by a nucleus does not result in a change in chemical properties of the nucleus but merely in the loss of a certain amount of radiant energy.
  Gamma particles are those that are given off by the spontaneous disintegration of a nucleus.
<number>
http://www-personal.umich.edu/~bielajew/NewStuff/EGS/gamma1.html
http://library.thinkquest.org/27917/content/gamma.htm

## Slide 8: Radiation Effects in the Primary System
Beta particles – high energy, high speed electrons emitted by a radioactive nuclei.
Positron – denoted in nuclear equations as . Has the same mass as an electron but with a positive charge.
Alpha particles consists of a helium nuclei.
<number>

## Slide 9: Radiation Effects in the Primary System
Crud formation and corrosion are not the only factors.
Water molecules can react under radioactive conditions to form oxygen-hydrogen substances.
The formation of oxygen and hydrogen products can lead to the formation of compounds with nitrogen.
Through neutron bombardment, the corrosion products and other impurities in the water can be made radioactive.
If a fuel clad defect exists, radioactive fission products can enter the coolant.
Suspended or dissolved solids or gases in the primary, must be removed to maintain a satisfactory chemistry environment.
<number>

## Slide 10: Radiolysis
Radiolysis is the dissociation of molecules by radiation.
Dissociation of water is a problem.
The moderating process of fission neutrons results in the breaking of hydrogen-oxygen bonds of the water molecules.
Gamma rays and some fission beta particles also contribute to water dissociation.
The dissociation products continually recombine to form water again.
Although the net decomposition is actually very small, it must be controlled to prevent free oxygen from forming in solution.
<number>

## Slide 11: Radiolysis
The significant factors affecting water reactions are the nature and energy of radiation and the temperature and composition of water. Water breaks down to form hydrogen and hydroxide ions:
H2O → H + + OH −
The resultant ions can produce hydrogen gas and hydrogen peroxide:
2H+ + 2OH− → H2 + H2O2
Hydrogen peroxide, H2O2, is a strong oxidizer that can cause an increase in the corrosion of plant metals.
At temperatures greater than 400°F, hydrogen peroxide dissociates rapidly to form hydrogen and oxygen:
H2O2 → H2 +O2
<number>
Notes: <number>

## Slide 12: Radiolysis
The recombination of hydrogen and oxygen is promoted by fission gamma radiation when the reactor is at power or by the residual gamma flux when the reactor is shutdown:
The net effect of the dissociation and recombination reactions is:
2H2O → 2H2 + O2
Oxygen concentration is minimized by maintaining about 25 cc of hydrogen per kilogram of water (to suppress oxygen formation).
The hydrogen also reacts with the oxygen introduced by the coolant.
The electrolysis reactions goes in both directions.
<number>
Notes: <number>

## Slide 13: Radiolysis
As we mentioned in module one, the equilibrium is affected by changes in concentration. If hydrogen is added the equilibrium will be shift towards the formation of water.
In the absence of radiation the equilibrium lies towards the formation of water.
Radiation increases the rate of the radiolysis reaction. It provides the activation energy for the reaction to take place.
A natural consequence of exposing pure water to ionizing radiation is production of both hydrogen and oxygen.
The addition of a base to control pH has essentially no effect on this feature (does not change the rate of the hydrolysis reaction).

## Slide 14: Reactions Involved in Radiolysis
Notes: <number>

## Slide 15: Radiolysis
The addition of hydrogen leads to the following reaction:
Hydrogen atoms from this equation subsequently react to form H2 and H2O by Reactions (3-7), (3-8), and (3-9).
Addition of hydrogen leads to the removal of free oxygen in solution.
Le Chateliers principle in equilibrium.

## Slide 16: Nitrogen Reactions
The presence of oxygen under irradiation can react with dissolved nitrogen in water.
Nitrogen can also react with excess hydrogen to form ammonia (NH3).
With oxygen it can form, nitric acid, HNO3
Formation of acid will decrease pH and accelerate the corrosion process.
If hydrogen remains, it undergoes an incomplete reaction with N2 to form small amounts of NH3.
If O2 remains after all the H2 has been consumed, the O2 - N2 reaction produces nitric acid.
<number>

## Slide 18: Lithium Production
Produced in the primary system.
Reaction will be covered later.
<number>

## Slide 19: Radionuclides in the Primary System
The first source is the activation of the water or impurities introduced with the water, such as corrosion products or chemical additives.
The second source of radioactivity is the release of radioactive fission products from the fuel or fuel cladding.
<number>

## Slide 20: Activation of Reactor Coolant
Oxygen can exist as oxygen-16 and a small fraction as Oxygen-18.
A proton reaction with oxygen-18 results in radioactive fluorine-18 plus a neutron:
Fluorine-18 decays back to oxygen-18 by emitting a beta plus particle and a gamma.
Fluorine-18 is not a long term contributor to reactor coolant activity since it has a half life of only 1.83 hours.
<number>

## Slide 21: Activation of Reactor Coolant
The most prevalent isotope of oxygen is oxygen-16 with an abundance in nature of 99.758 percent. When bombarded by a neutron, oxygen-16 transforms to nitrogen-16:
Nitrogen-16 decays to oxygen-16 by emitting a beta minus particle and a gamma ray.
The energy of the gamma is 6.13 MeV and the half life of nitrogen-16 is 7.1 seconds.
Nitrogen-16 is one of the greatest radiation hazards in the primary system because they are a great number of oxygen-16 in the system.
Shielding requirements for the Reactor Coolant System are primarily based on the energy of the gamma produced in this reaction.
<number>

## Slide 22: Activation of Impurities
Other impurities in the primary system come from make-up water or are introduced with chemical additives to the system.
Argon-41 decays through beta minus emission with a half life of 1.83 hours.
Argon is introduced into the system if air has entered the coolant.
<number>

## Slide 23: What is fission?
A nuclear reaction in which an atomic nucleus, especially a heavy nucleus such as an isotope of uranium, splits into fragments, usually two fragments of comparable mass, releasing from 100 million to several hundred million electron volts of energy.
Nuclear fission is a nuclear reaction in which a heavy nucleus (such as uranium) splits into two lighter nuclei (and possible some other radioactive particles as well).
<number>
http://physics.about.com/od/glossary/g/nuclearfission.htm
http://www.thefreedictionary.com/fission

## Slide 24
<number>

## Slide 25
Fusion - A nuclear reaction in which nuclei combine to form more massive nuclei with the simultaneous release of energy.
<number>

## Slide 26: Radiation Terminology
<number>
Beta particles – high energy, high speed electrons emitted by a radioactive nuclei.
  Beta emission is equivalent to a neutron being converted to a proton and an electron.
Positron – denoted in nuclear equations as . Has the same mass as an electron but with a positive charge.
  A positron emission is equivalent to the conversion of a proton to a neutron. Also known as a Beta-plus emission. An example of it is as follows:
Alpha particles consists of a helium nuclei.
Same molecular weight but a different atomic number.
Notes: <number>

## Slide 27: Radiation Terminology
Atoms with more than 83 protons will emit alpha particles (Helium nucleus)
If the ratio of numbers of neutrons divided by the number of protons is too large, beta emission will take place
  for atomic number less or equal to 20, Neutrons/Protons > 1.1
  for atomic number between 21 and 50, Neutrons/Protons > 1.5).
Positron emission – for a ratio below one for smaller compounds or below 1.5 for compounds with an atomic number between 21 and 50.
<number>

## Slide 28
<number>
Beta Emission
Positron emission or electron capture
Electron Capture – the decay of an unstable nucleus by picking up an electron from an inner orbital of an atom. In this case, a proton combines with an electron to give a neutron.
All elements with an atomic number greater than 83 will not be stable and experiences alpha decay.
That does not mean that alpha emission is limited to larger atoms.
A-Z = # of neutrons
http://wwwndc.jaea.go.jp/CN10/CN021.png

## Slide 29
<number>
Notes: <number>

## Slide 30
<number>

## Slide 31
<number>
Problems:
1. Predict the expected type of radioactive decay for each of the following nuclides:
  Ca-47
  Al-25
2) Sodium-23 is the only stable isotope of sodium. Predict how sodium-20 and sodium-26 will decay.

## Slide 32: Problems 3
Rubidium-87, which forms about 28% of the natural rubidium, is radioactive, decaying by the emission of a single Beta-minus particle to strontium -87. Write the nuclear equation for this decay of rubidium-87.
<number>

## Slide 33: Problem 4
Fluorine-18 is an artificially produced radioactive isotope. It decays by emitting a single positron. Write the nuclear equation for this decay.
<number>

## Slide 34: Problem 5
Radon is a radioactive noble gas formed in soil containing radium. Radium-226 decays by emitting a single alpha particle to form radon-222. Write the nuclear reaction for the decay of Radium-226.
<number>

## Slide 35: Activation of Impurities
Oxygen enters the system with the feed water or is produced during the radiolysis of water.
Nitrogen-13 beta plus decays in 9.97 minutes.
<number>

## Slide 36: Activation of Impurities
<number>
If loose corrosion products pass through the core, they can become activated.
The most significant radionuclide are manganese-56, iron-59, and cobalt-60.
The reactions are equivalent for each of them. For Cobalt:
The Cobalt-60 then decays by either gamma or beta minus emission.
Notes: <number>

## Slide 37: Activation of Impurities
Cobalt is a constituent of the alloy stellite which is used in reactor coolant pump components and CRDM jack shafts.
Other radioactive isotopes that can be produced from activation of crud are chromium-51, tungsten-187, zirconium-95, and silver-110.
Chromium is present in stainless steel and Inconel.
Zirconium is present in zircaloy.
Tungsten is a component of stellite.
<number>

## Slide 38: Activation of Impurities
The presence or absence of any of these isotopes serves as an indicative of the integrity of the components in the plant.
The presence of silver-110 indicates control rod cladding failure.
<number>

## Slide 39: Tritium Formation
The isotope of hydrogen that contains two neutrons and one proton is called tritium.
Exposure of water containing tritium to the atmosphere produces tritium oxide. If a person breathes tritium oxide, it will exchange with the hydrogen in the lungs.
Tritium in the body continuously releases radiation.
This radiation can not be controlled.
It has a half life of 12.33 years.
<number>

## Slide 40: Tritium Formation
<number>
Tritium is produced by three activation processes and in the fission process.
Deuterium, a hydrogen isotope with one neutron, represents 0.015 percent of all naturally occurring hydrogen.
When deuterium absorbs a neutron, it converts to tritium:
This process produces less than one percent of the tritium found in the water.

## Slide 41: Tritium Formation
The largest portion of tritium results from reactions associated with Lithium and Boron.
Lithium present in the primary system comes mostly from the addition of lithium hydroxide, LiOH, used as the pH control agent and from the reaction:
<number>

## Slide 42: Tritium Formation
Natural lithium contains 7.5 percent of the isotope lithium-6. Upon absorbing a neutron, lithium-6 produces tritium:
To minimize tritium levels in the primary, lithium hydroxide is enriched to 99.9 percent lithium-7.
The remaining 0.1 percent lithium-6 contributes about 2 percent of the tritium produced.
<number>

## Slide 43: Tritium Formation
The bulk of tritium present in the primary comes from a reaction of boron, the chemical additive used for reactivity control.
Upon absorbing a neutron, the boron-10 isotope typically transforms to a lithium-7 nuclide and an alpha.
In some cases, though not predominantly, boron-10 and a neutron produce two alphas and a tritium atom:
This reaction accounts for about 80 percent of the tritium found in the primary system.
This tritium diffuses through the fuel cladding into the coolant.
<number>

## Slide 44: Fission Fragments
Most products produced from fission events are radioactive, undergoing an average of three beta minus decays to reach stability.
One of the major concerns of the plant design is the development of safe means of containing the fission products first within the fuel rod, then within the primary system, and finally within the Containment Building.
The zircolay-4 fuel cladding prevents excessive contamination of the reactor coolant with radioactive fission fragments.
Some radioactivity will always pass through the cladding due to uranium impurities in the zirconium.
The major potential problem is the uncontrolled escape of fission fragments through fuel element defects.
Two factors determine the radiological hazard posed by a “plume” of released gas: the total activity (how many curies) and how powerful the gammas and electrons emitted are (average energy per disintegration).
A "plume" is a release of gas into the atmosphere from a point source.
<number>

## Slide 45: Fission Fragments
Isotopes with short half-lives (< 15 minutes) or low energy emissions are of relatively small concern since they will either decay off before reaching the public or cause a relatively low dose when they do decay.
Iodine-131 and iodine-133, with half lives of 8.041 days and 20.8 hours respectively, are two of the most important biological hazards because Iodine tends to concentrate in the thyroid when ingested.
<number>

## Slide 46: Fission Fragments
Elemental iodine, I2, is formed inside the fuel rod as a gas. During normal operation, any iodine gas leaking from the fuel enters the coolant at a slow rate.
Iodine reacts from gas to a solid suspended in water (when it reaches the cooling system).
In the event of a ruptured fuel rod coupled with a loss of coolant accident, iodine gas and solids would be released into containment.
<number>

## Slide 47: Fission Fragments
Other biologically damaging fission fragment radioisotopes are cesium-137, cesium-138, strontium-89, and strontium-90. Cesium concentrates in muscle tissue and strontium concentrates in bones.
<number>

## Slide 48: Dose Equivalent I-131
“Dose Equivalent I-131 shall be that concentration of I-131 (in microcuries/gram) which alone would produce the same thyroid dose as the quantity and isotopic mixture of I-131, I-132, I-133, I-134 and I-135 actually present...”.
E − (“E-bar”), or “Average Disintegration Energy” is defined as follows:
  “Ē shall be the average (weighted in proportion to the concentration of each radionuclide in the reactor coolant at the time of sampling) of the sum of the average beta and gamma energies per disintegration (in MeV) for isotopes other than iodines, with half-lives greater than 15 minutes, making up at least 95% of the total non-iodine activity in the coolant.”
<number>

## Slide 49: Dose Equivalent I-131
<number>
This E-bar value provides a rough estimate of biological damage (whole body dose) which will be caused by each curie of non-Iodine activity released.
The dose limits for the public in 10CFR100 will not be exceeded if RCS activity is less than 100/E-bar μCi/ml.
It should be noted that this 100/E-bar limit corresponds to 1% failed fuel and is many orders of magnitude higher than the RCS specific activities normally encountered, even with several minor fuel leaks (about 0.01 μCi/ml).

## Slide 50
The approximate values for Dose Equivalent I-131 and E under steady state conditions:
  E=0.1 MeV/disintegration (Cycle 15)
  DE I-131 = 1.64 x 10-4 microcuries/gram
The true limit is shown on CR2.1
<number>

## Slide 51
<number>

## Slide 52: What is a Curie?
1 Curie = 3.7 x 1010 decays/second
1 microcurie = 10-6 Curies
The unit is named after Pierre and Mary Curie.
Mary Curie developed techniques to isolate radioactive isotopes and discovered two radioactive elements, radium and polonium.
Henry Becquerel discovered that uranium salts emitted light similar to x-rays and this was not dependent on the addition of an external energy source.
Mary Curie studied Uranium as part of her thesis and she discovered that Uranium makes the air around it able to conduct electricity.
Then, she found that radioactivity is a function of the amount of material and not the interactions between molecules. (Energy comes from the atom itself).
<number>

## Slide 53: Primary Plant Chemistry Control
<number>

## Slide 54: Chemical Additives Added to the System
Usual additives include hydrogen, boric acid and lithium hydroxide.
Boric acid is used to conduct reactivity in the primary system.
It has little effect in pH (it is a very weak acid)
The addition of hydrogen removes free oxygen by two means.
  First, hydrogen combines with free oxygen to form water in the presence of gamma rays.
  Second, an excess amount of free hydrogen actually helps reduce the amount of oxygen produced by the radiolysis of water reactions.
  Hydrogen concentration is reduced prior to shutdown.
Lithium hydroxide is added for pH control.
  Corrosion of metals is reduced in a neutral to slightly basic pH environment.
  A higher pH also tends to minimize the deposition of crud which fouls heat transfer surfaces and clogs mechanical components.
<number>

## Slide 55: Chemical Additives
At temperatures below 200ºF, hydrazine can be added to react with oxygen.
At temperatures greater than 200ºF, hydrazine will disintegrate making it a bad oxygen scavanger.
<number>

## Slide 56: Specific Parameters
Generally include the following:
  pH, dissolved oxygen, hydrogen, total gas content, conductivity, chlorides, fluorine, boron, and radioactivity.
  For the parameters indicated, control is generally achieved by one or more of three basic processes.
    Ion exchange in the primary system demineralizer(s) or by supplemental chemical additions
    Oxygen scavenging by hydrogen or hydrazine addition
    Degassification

## Slide 58: pH Control
The reason for controlling pH in the reactor coolant system is to minimize and control corrosion.
A low pH promotes rapid corrosion by deteriorating or "stripping off" the protective corrosion film, and second, corrosion products such as ferrous oxide (Fe3O4), which is predominant in the corrosion film, are highly soluble in an acidic solution.
In facilities that use chemical shim reactivity control (chemical shim involves the addition of boron in the form of boric acid) the pH is maintained at a much lower value.
  A low pH is necessary because of the large amounts of boric acid added to the reactor coolant.
  pH in these facilities is maintained as high as possible consistent with the reactivity requirements of the nuclear facility, with pH range from 5 to 7 being common.

## Slide 59
In facilities using aluminum components, pH is maintained on the acidic side of the scale because of the corrosion characteristics of aluminum.
Regardless of the pH range maintained, most facilities use an ion exchange process (described in Module 4) to help control pH.
For the high pH facilities, the most common means of control is the use of a lithium or an ammonium form cation and a hydroxyl form anion.
When lithium is used, it must be 7Li because other lithium isotopes produce tritium, which represents a significant biological hazard to personnel.

## Slide 60: Dissolved Oxygen
The base reactions of concern regarding high concentrations of dissolved oxygen are the following:
Dependent on both the concentration of oxygen and temperature.
Reaction (3-19) is predominant at high temperatures (>400ºF) in the presence of lower oxygen concentrations.
Below 400ºF we form Ferric Oxide (Fe2O3)
In either of the reactions, the corrosion rate is accelerated by increased concentrations of dissolved O2 and can be aggravated further by the presence of other substances that may be present in the system.

## Slide 61: Dissolved Oxygen
In addition to the direct contribution to corrosion, oxygen reacts with nitrogen to lower the pH of the reactor water, which also results in an increased rate of corrosion.
Oxygen and nitrogen react to form nitric acid by the following reaction.
Concentration may be monitored on a continuous basis by using an in-line analyzing system or periodically by withdrawing a sample volume and analyzing that sample.
Hydrogen gas (H2) and hydrazine (N2H4) are the scavenging agents normally used to eliminate dissolved oxygen from the reactor coolant system.
Hydrazine decomposes at temperatures above 200ºF.
At higher temperatures we use hydrogen as an oxygen scavanger.

## Slide 62: Dissolved Oxygen
A boiling water reactor (BWR) facility is susceptible to corrosion, resulting from dissolved oxygen, in the same reactions as are present in a pressurized water reactor (PWR).
However, because of the design of these facilities the use of chemical additives is prohibited because continuous concentration would occur in the reactor vessel due to boiling.
Boiling would result in a plating out process, and the irradiation of these concentrated additives or impurities would create an extreme environment of radiation levels as well as adverse corrosion locations.
By the very nature of operation of a BWR facility, the buildup of high concentrations of dissolved oxygen is prevented.
Boiling is an effective means of removing gases from a solution.
BWR facilities minimize the introduction of dissolved oxygen by pre-treating makeup water by some method.

## Slide 63: Dissolved Oxygen
The large oxygen concentrations measured in the steam system result primarily from the radiolysis of water according to Reaction (3-12), and as operation is continued, the equilibrium concentration of 100 ppb to 300 ppb is established.

## Slide 64: Example of a BWR

## Slide 65: Total Gases
Total gas is the sum of all gases contained in the coolant system and is made up primarily of hydrogen (H2), nitrogen (N2), argon (Ar), and oxygen (O2).
The small amounts of fission gases (Kr and Xe) normally present in the system may also contribute to the total gas concentration; however, under normal conditions these are essentially undetectable.
Total gas is of concern because high concentrations can result in the formation of gas pockets in areas that are high points of the system where low or stagnant flow conditions exist.
In extreme concentrations of total gas, loss of pump priming and cavitation can occur with resultant mechanical pump damage.
Reduction of total gas concentrations in PWRs is normally accomplished by the venting of a steam space.
This process of reducing the total gas concentration is generally referred to as degassification.
Degassification is not normally required in a BWR because of its design.

## Slide 66: Conductivity
Conductivity measurements provide quantitative rather than qualitative information because it is possible to determine the total conductivity of the ions present, but not the specific types of ions present.
Reactor coolant conductivity is normally controlled at a level as low as practicable and consistent with pH.
Excessively high conductivity levels are an indication of the presence of undesired ions.
  Must locate the source of the impurity because, in addition to other chemistry problems, it contributes to general corrosion by increasing the reaction rates of the electrochemical cells.
  Parameters to check: Chloride ions, fluoride ions, pH, etc.
Feed and bleed is usually done to decrease conductivity.
  Water is added to and drained from the facility at the same time.
Low conductivity is also an indicator of a potential problem because, in high purity basic systems, the only possible cause of low conductivity is a low pH. (Formation of an acid)

## Slide 67: Conductivity
Conductivity decreases even more than would be expected because of the formation of NH4NO3.
NO3- is not as conductive as OH-, so the NH4NO3 results in a lower conductivity than NH4OH.
<number>

## Slide 68: Chlorides
The reason for maintaining the chloride ion concentration at the minimum level practicable is that several forms of corrosion are affected by the chloride ion, and the type of greatest concern is chloride stress corrosion.
When high levels of Cl- are suspected, or detected, immediate steps must be taken to eliminate the source and remove Cl- from the system because of the potential consequences.
If Cl- is present in the reactor coolant system, one method of removing it is to initiate a feed and bleed operation after determining that makeup water supplies are not the source of contamination.
<number>

## Slide 69
Additional problems associated with feed and bleed operations include changes in pH and a loss of H2 from the reactor coolant system during the cleanup.
Less hydrogen leads to a greater risk of corrosion.
<number>

## Slide 70: Fluorine
High levels of F- are potentially hazardous for two reasons.
  F- promotes corrosion of zirconium by a stress corrosion mechanism at the inner surface of the clad
    fluorine can be introduced to this region because of the existence of small defects or "pinholes" that cannot be completely avoided in the fuel clad.
  F- is a major contributor to radiation levels of the reactor coolant. Radioactive 18F is produced by a proton, neutron reaction with 18O.

## Slide 71: Fluoride
Removed by feed and bleed or increased flow through the ion exchanger system.
Removal by ion exchange, however, is not as effective as for Cl- because of the lower affinity of F- for exchange.

## Slide 72: Radioactivity
Conditions that result in increase radioactivity include
  These include increased corrosion, crud bursts, fuel element defect or failure, and improper operation of the ion exchanger (where installed).
Maintained within acceptable limits using an ion exchanger.
For units without ion exchangers
  These include processes such as chemical cleanup followed by feed and bleed with subsequent disposal procedures and reactor shutdown in severe cases.
Reactor coolant gaseous activity is also monitored, and it provides an indication of cladding failures and the introduction of air during reactor operation.
  Gaseous activity levels are normally controlled by degassification.
Limits are established in most reactor facilities to operate the reactor safely, to limit radioactive releases to the environment, and to prevent excessive personnel exposure during operation and shutdown.

## Slide 73: Tritium
Tritium occurs naturally in the environment.
They include light-water reactors, heavy-water reactors, fuel reprocessing facilities, and production reactors.

## Slide 75
Tritium decays by emitting a weak beta particle together with an antineutrino.
The product is helium-3.
The decay of 1 mole of T2 yields 2 moles of helium.
Hydrogen atoms or diatomic hydrogen molecules and some larger hydrogen-bearing molecules dissolve interstitially; that is, they diffuse into a structure and locate between atoms or molecular frameworks.

## Slide 76: Abnormal Chemistry Conditions
Actions taken regarding one specific chemistry parameter may affect more than that parameter (such as feed and bleed operations).
Will consider the effect of injection of air, fuel element failure, and overheating of resin and discuss the probable changes to other chemistry parameters that may occur.

## Slide 77: Injection of Air
When sufficient oxygen is added to deplete the hydrogen inventory, acidic pH results in those facilities where high (basic) pH is maintained.
The reduced pH causes a change in solubility of the corrosion film on facility materials and results in part of this film being released for transport throughout the coolant system.
  Results in increase radiation levels, larger conductivity and lowering of the ion exchange efficiency.
  Conductivity increases because many of the corrosion products are released in an ionic or radical form and are capable of conducting electricity.
  Ion exchanger efficiency decreases because the increased crud inventory consists of both particulate and colloidal products.
    only about 90% effective as a filter
    Effluent radioactivity will be higher
    Crud in colloidal form will not be removed by ion exchanger

## Slide 78
Because air contains primarily N2 and O2, the gas inventory in the system increases.
Hydrogen levels decrease because of reactions with both O2 and N2.
With large amounts of air we introduce Argon into the system.
  Can become activated and increase gaseous radiation.
Once crud is released it remains in the system. We can reverse the dissolved ions but cannot reverse the damaged caused to the corrosion layer.

## Slide 80: Fuel Element Failure
If a defect were present or a failure of a fuel element occurred, large amounts of fission products would potentially have a path to the coolant system.
Significant changes would occur within the reactor coolant chemistry parameters.
When routine gaseous radioactive levels are monitored, an increase in this parameter's value would be seen.
  Many of the fission products are gaseous, and these gases are more mobile than particles of exposed fuel.
The other parameter that may change is the ion exchange efficiency (where utilized), because many of the fission products released have a lower affinity for the exchange sites on the resin beads than the exchange anion or cation.

## Slide 81: Resin Overheating
Basically the resin of an ion exchanger is an inert polystyrene structure with ion exchange sites "loosely" attached.
  stable up to fairly high temperatures (approximately 300 ºF), but the active exchange sites are not.
  Anion and Cation Resins
  The anion resin begins to decompose slowly at about 140 ºF, and the decomposition becomes rapid above 180 ºF.
  The cation resin is stable up to about 250 ºF.
  Decompose well below the operating conditions.

## Slide 82: Resin Overheating
Decomposition reaction – forms am alcohol form of the resin that cannot exchange ions. Produces trimethyl amine that reacts further as shown in the reaction below:
pH can increase significantly due to the release of OH- ions.
The other product of resin breakdown, [R - CH2N(CH3)2], is an amine with exchange capabilities considerably less than the original form of the resin.
If higher T is sustained the resin will be damaged.

## Slide 83: Resin Overheating
Signs of resin overheating
  Reactor coolant Cl- levels would probably increase as a result of thermal breakdown and subsequent release.
  Decreased ion exchange capability.
  Radioactivity levels will increase due to release of previously filtered radioactive impurities.
  pH would likely decrease because of the release of H+ ions from the resin complex and may cause acidic conditions in the reactor coolant if the temperature is sufficient (>250 ºF).
  If overheating takes place resin must be removed from the system.
  The resin must be replaced prior to placing the ion exchanger back in service after overheating.

## Slide 84: Water Purification
Includes:
  Filters
  Ion exchangers
  Gas Strippers
<number>

## Slide 85: Water Filters
Sediment filters – to remove particulate from the water. Do not remove dissolved pollutants.
  Fiber filters
  Ceramic filters
Activated carbon filters – used to remove organics from solution. It adsorbs organics.
  Granulated Activated Carbon – GAC
    Bed of AC particulate used to remove organics, some chlorine, and undesirable taste and odor.
    Advantages: Affordable, improve taste and odor, low maintenance, do not waste water, do not require electricity.
    Disadvantages: 1) Channeling of water (results in water that is not purified), 2) pockets of contaminated water (any variation in pressure can release these pollutants), 3) difficult to tell when the filter has gone bad.
<number>

## Slide 86: Activated Carbon Filters
Solid Block Activated Carbon (SBAC)
  Provide large surface area.
  High contact time.
  Smaller pore size (can trap contaminants easier than GAC).
  Do not waste water.
  Affordable
  Structure allows for easier removal of contaminants
<number>

## Slide 87: Disadvantages of SBAC
Cannot remove salts.
Cannot operate with hot water.
Loose effectiveness over time.
<number>

## Slide 88: Filters
In the water purification system, filters are used to remove particulates.
Once they clog, filters must be replaced.
<number>

## Slide 89: Ion Exchange
An ion exchanger consists of a metal cylinder filled with resin beads.
The primary function of a resin bed is to remove dissolved ionic materials.
The resin is an ion exchange material, which has the ability to exchange one ion for another, hold the removed ion temporarily in chemical combination, not in the RCS.
The positively charged ions are referred to as cations and the negatively charged ions are called anions.
The function of the ion exchange process is to remove ionic impurities from the water through chemical reactions.
The resin is written symbolically as (cation)+ - (R-) or (anion)- - (R+).
<number>

## Slide 90: Ion Exchange
Examples of resins:
The resin can be cation exchange or anion exchange.
The ions attached to the resin beads are replaced by ions in the water.
<number>

## Slide 91: Ion Exchange
Since lithium hydroxide is the chemical used for pH control, the ion exchangers connected to the RCS use a mixed bed of Li+ - R- and R+ - OH- (Li - OH) resins.
This allows for the exchange of ions in solution by hydroxide and lithium ions.
<number>

## Slide 92: Demineralization using Ion Exchange Resins
Demineralization, (see Fig CR2.10) as applied to water treatment, is the removal of essentially all inorganic salts.
In ion exchange demineralization, hydrogen cation exchange converts dissolved salts to their corresponding acids, and basic anion exchange removes these acids.
Ion exchange demineralization of most fresh water supplies is widely used because it is less expensive than distillation.
<number>

## Slide 93
Purpose of demineralization
  Removal of ionic substances
  Reduction of conductivity
  Control of pH
  Filtration of corrosion products.
<number>

## Slide 94: Ion Exchange and De-Ionization Process
De-ionization removes all ions in the water.
Contains two parts: an anion exchange and a cation exchange unit.
Soft water – does not contain Ca and Mg ions.
De-ionized – no ions.
Every soft water is not demineralized but every de-ionized water is soft water.
DI water is used in chemical processes like chemical production, pharmaceuticals, electroplating, leather products, …
<number>

## Slide 95: The Process
The cation exchange resin removes the cations and replaces them with H+ ions (protons) or a specific cation like Li.
The hard water passes through the anion exchange resin where the anions are adsorbed and OH- (hydroxide ions) are released.
The net result is the replacement of water hardness with H2O molecules.
<number>

## Slide 96: Regeneration of DI unit
Diluted acid is used to regenerate the cation exchange resin (HCl or H2SO4).
Column is rinsed with DI water to remove the cations.
The anion resin is cleaned by adding a diluted solution of NaOH. This results in the exchange of anions with OH-.
The anion exchange resin is rinsed with DI water.
<number>

## Slide 97: Advantages: DI Process
Very efficient in removing ions
Little water is wasted
Reliable performance
Selected impurities can be removed.
Process can be used under acidic and basic conditions.
Hardness is reduced to about 2 ppm.
Excellent to produce water for boilers.
<number>

## Slide 98: Disadvantages: DI Process
Expensive: equipment and chemicals used.
Impurities in the water results in a decrease output.
Requires low turbidity (like zeolites) below 10 ppm. (Coagulation and filtration must be used with higher turbidity)
Does not remove bacteria, H2S, sand, lead, nitrate, pesticides and other organic and inorganic compounds.
<number>

## Slide 99: Organic Contamination
Organic chemicals (both chlorinated and non-chlorinated hydrocarbons), lubricating oils, and resins that decompose under heat and/or radiation environment result in high conductivity, low pH, high hydrogen levels, and high radiation levels.
Under reactor conditions, organic compounds can undergo hydrolysis with bond breakage (due to thermal and radioactive conditions). Tar can form in the system.
If the organic compound contains chlorine, during decomposition the chlorine may become chloride ions (increases conductivity of water).
Anion Resin
  Breaks down at lower temperatures than Cation resin.
  Decomposition results in the presence of amines in colloidal and/or solution form.
  Under high temperature and neutron flux conditions present in the reactor, the amines breakdown into ammonia and dilute nitric acid.
  Results in a reduction in pH and a significant increase in conductivity.
  Breakdown of anion resins can occur either due to temperature or neutron flux.
  CH3NH2
<number>
C-N
H
H
H
H
H

## Slide 100: Organic Contamination
Cation Resin
  Breaks down to produce ionic functional groups under temperature or radiation. The functional groups further react to produce dilute sulfuric acid resulting in low pH and high conductivity.
  Chlorinated Hydrocarbons (typical of many cleaning solvents, dye penetrants, Etc)
  Intrusion of resins from the demineralizer into other systems (i.e., RCS) is restricted by the use of retention elements internal to the Demineralizer (see Fig CR2.11) and a filter downstream of the demineralizer.
<number>

## Slide 101: Organic Contamination
It is not only due to the resins but also from cleaning agents and lubricants.
If excess organics enter the reactor system results in:
  Water chemistry of the coolant exceeds specifications.
  Forced shutdown of operating plants.
  Probable intergranular stress corrosion in stainless steel.
  Prolonged shut down while cleaning with large amounts of water in reactor coolant and auxiliary components.
  Fouling of demineralizers.
    Fouling – accumulation of unwanted materials in a surface. In the demineralizers the organic materials accumulate in the resin bed. The organic matter becomes irreversibly attached to the resins causing a decay in the performance of the demineralizer.
  Potential deposition of breakdown products on reactor coolant system materials and in crevices. These may be difficult to cleanup and can contribute to long-term continued localized corrosion and stress cracking.
<number>

## Slide 102
<number>
See the article: http://nzic.org.nz/ChemProcesses/water/13D.pdf

## Slide 103: Resin Intrusion into the Steam Generators
Resins are an organic compound with an ionic portion. The resin in the plant is similar to the strongly acidic polystyrene resin in the previous slide.
If portions of the resin is released into the coolant, when the resin is exposed to a neutron flux and high temperatures it decomposes and releases sulphonated compounds. This decreases the pH of the water.
<number>

## Slide 104: Resin Intrusion at VC Summer
An incident occurred in July of 1989.
The plant experienced unusually high sulfate (SO42-) and conductivity.
This puts all plant components at great risk of corrosion.
The resin intrusion was caused by the mispositioning of a steam generator blowdown demineralizer by-pass valve following maintenance.
Sulphate levels reached 10.7 ppm and a cation conductivity of 120 microSiemens.
<number>

## Slide 105: Actions Taken after the Incident
Strainers were installed in the inlet piping of the SG blowdown demineralizers to prevent siphoning of resin.
Valves and components manipulated during a tagout will be given two independent checks before the system is returned to service.
Improvements will be made in the methods used to determine the actual volume of resin in a demineralizer tank. Ability to determine the actual volume of resin loss would help quantify the magnitude of any future problem of this type.
<number>

## Slide 106: Ion Exchange System
The flow rate through the resin bed must also be restricted to an upper limit to prevent channeling of flow.
The ability of an ion exchanger to perform its designated function is measured by its decontamination factor, DF.
The decontamination factor is the ratio of the activity or concentration of the solution entering the ion exchanger to the activity or concentration of the solution leaving the exchanger:
<number>

## Slide 107: Cation Demineralizers
Resin that contains a cation exchanging resin. All the cations are exchanged with protons.
The ions in solution are chemically bonded to the resin and at the end we get ion free water (when the water passes through a cation and anion resin).
The water may still contain non-ionic compounds that must be removed with other processes.
<number>

## Slide 108: Mixed Bed Demineralizers
Contain a cation and an anion exchange resins mixed together.
In a mixed bed demineralizer the ion exchange capability is equivalent to the two exchange resins connected in series but the water quality is greatly improved.
Conductivity is normally less than 0.06 microhms per centimeter.
<number>
http://www.tpub.com/content/doe/h1018v2/css/h1018v2_108.htm

## Slide 109
<number>
Miscellaneous Mechanical Components DOE-HDBK-1018/2-93 DEMINERALIZERS
Figure 14 Regeneration of a Mixed-Bed Demineralizer Rev. 0 ME-05 Page 27

## Slide 110: Gas Stripping
Gases dissolved in the coolant must be removed.
These gases include oxygen, nitrogen, argon, hydrogen, xenon, and krypton, some of which must be removed from the coolant by the process of gas stripping.
Gas stripping involves breaking up the water into small droplets and heating it.
While heating the gases come out of solution and are vented up.
Radioactive gases are collected in a radioactive gas system.
<number>

## Slide 111: Chemistry of the Secondary System
The objectives of secondary plant chemistry control are:
  Prevent the failure of secondary plant materials or equipment by destructive mechanisms of corrosion.
  Minimize the thermal, hydraulic, and clogging effects of sludge production and deposition.
  Minimize effects on turbine due to carryover from the steam generator.
  Ensure the quality of the secondary water is maintained.
<number>

## Slide 112: Chemistry of the Secondary System
Water is present in the form of steam from the gas generator to the inlet of the condenser. After the condenser the water exists in the liquid form.
Bad chemistry control can result in corrosion and component failure.
Impurities come from corrosion products, impurities in the chemical additives, impure makeup water, leakage in the main or auxiliary condensers. Another source is contact with air during maintenance.
<number>

## Slide 113: What happens with the impurities in the Secondary Unit?
Impurities enter the system and when the water goes through the boiling process in the steam generator the impurities concentrate.
The concentrated chemicals chemically attack the surface of the metal.
The steam generator tubes are the boundary between the radioactive reactor coolant and the secondary coolant.
  A tube leak or rupture in the steam generator results in a radioactive leak to the secondary plant as well as a reduction in plant efficiency.
<number>

## Slide 114: Chemical Additives in the Secondary Plant
The chemicals principally added to the secondary are Carbohydrazide, Methoxypropylamine, Ammonium Chloride, and Ammonia.
Ammonium Chloride (not currently added) - can be added to the steam generators to reduce stress cracking corrosion in the crevice areas.
  The cations in the crevice attract anions like hydroxides resulting in very caustic conditions (high pH).
  Cations accumulated in crevices react with the chloride ion released by ammonium chloride. This neutralizes the cations resulting in less corrosion.
<number>

## Slide 115: Chemical Additives in the Secondary System
Methoxypropylamine, (MPA) is added for pH control during steady state operations MPA more readily distributes itself in the two-phase areas of the secondary plant such as the HP Drain System.
It is soluble in water and in organic compounds.
<number>
http://www.huntsman.com/performance_products/Media/MOPA_(Methoxypropylamine)_(4-08).pdf

## Slide 116: Chemical Additives in the Secondary System
Carbohydrazide is added to the secondary at V.C. Summer to remove oxygen.
  Oxygen is removed to prevent general corrosion and other types of corrosion.
  Used as a safer replacement to hydrazine.
  Lowers corrosion rate by oxygen scavenging reactions.
  Surface-chemistry reactions provide material passivation.
<number>

## Slide 117: Chemical Additives in the Secondary System - Carbohydrazide
Reactions with carbohydrazide include:
At higher temperatures carbohydrazide decomposes to hydrazine which also reacts with oxygen.
At lower temperatures, carbohydrazide is the main oxygen scavanger.
<number>

## Slide 118: Chemical Additives in the Secondary System - Carbohydrazide
Passivation reactions with carbohydrazide include
Hydrazine has been replaced due to stricter regulations about its use.
<number>

## Slide 119: Chemical Additives in the Secondary System - Blowdown
Blowdown is a simple process of water being drained out by an open pipe at the bottom of the steam generator.
Impurities and corrosion products accumulate in the steam generator. If left unchecked they can carry over and cause problems with the turbines and deposit of solids on the turbine blades.
Carryover is the movement of particles in moisture making its way from the steam generator to the steam system.
During blowdown solids accumulated in the steam generator can be removed and it also removes chlorine and other impurities.
<number>

## Slide 120: Service Water Cooling System Organic Treatment
The purpose of the service water system is to cool the heat exchangers.
The coolant water must be treated to avoid the growth of organic species like asiatic clams.
Treatment is accomplished by injecting a molluscicide, (Clam-Trol CT-2) at the trash racks located at the entrance to the SW intake tunnel structure.
<number>

## Slide 121: Operations
The chemist is responsible for making sure that samples are collected at the correct time and correct frequencies.
Reviews the data against the technical specifications to determine if further action is needed.
<number>

## Slide 122: Primary Sampling and Analysis
Sampling is performed to analyze that the water has proper chemical make up or to detect discrepancies in the primary system.
Some of the chemistry-related variables the analysis will determine are dissolved oxygen, hydrogen, lithium, chloride, and boric acid concentrations.
Sampling also measures total suspended solids, total dissolved gases, pH, and solution conductivity.
Radiochemistry variables that are checked are Dose Equivalent I-131 and E-bar.
Depending of the results, corrective actions may need to be taken.
<number>

## Slide 123: Primary Sampling and Analysis
Frequency of sample is increased during times where actions that are expected to increase RCS activity are taking place and when the RCS or Secondary system activity are reaching the Technical Specification limit.
Since fuel rods frequently “burp” out iodine from the gap between the clad and the fuel pellet during power changes, chemistry must be directed to sample for dose equivalent Iodine between 2 and 6 hours following any power change of >15%.
Operation may continue with DEI-131 > 0.059 μCi/ml (limited by Figure CR2.6) for up to 48 hours, but sampling frequency must be increased to every four hours.
Note that Dose Equivalent I-131 above 12.8 μCi/gm requires declaration of an NUE per EPP-001.
<number>

## Slide 124: Primary Sampling and Analysis
Non-Iodine activity is routinely checked by conducting a “Degassed Gross Activity” 15 minutes after a RCS sample is obtained.
This result is compared to the 100/E-bar limit on specific activity.
The limit is close to 100/E-bar but the normal readings is close to 0.01 µCi/gm.
It would be highly unusual to challenge the 100/E-bar limit without having Dose Equivalent Iodine already high enough to require shutdown:
  A fuel failure will usually exceed the Iodine limit; only a gross crud burst (corrosion products shaken off core) or a fuel failure during a startup could exceed 100/E-bar first.
<number>

## Slide 125: Primary Sampling and Analysis
The Failed Fuel Action Plan (FFAP), SAP-154 has several escalating levels of required corrective actions
  increasing CVCS (Chemical Volume Control System) letdown flow,
  VCT (volume control tank) purge rate,
  realign secondary to minimize release rate,
For the FFAP to be activated the iodine levels must be high enough (the highest action level is activated at 0.5 μCi/gm DEI-131).
Do not ask on test
<number>

## Slide 126: Secondary Sampling and Analysis
The analysis is used to detect any discrepancies in the chemistry environment.
The secondary water is purified through condensate polishers.
Secondary water is passed through these polishers following a shutdown or when the plant is operating below 45 percent power because they are sized to handle only 45 percent of full flow.
Above 45%, the ion exchanger must be shut down.
By the Technical Specifications, Steam Generator activity must be less than 0.1 microcuries/gram Dose Equivalent I-131. If activity exceeds 0.01 μCi/gm (1/10 of the limit), sampling frequency must be increased.
<number>

## Slide 127: SG Chemistry during Inactive Periods
During operation maintaining the chemistry of the SG is simple.
  Well mixed system.
  High pressure keeps oxygen from entering the system.
To prevent corrosion, the steam generator must also be protected during periods of inactivity (prevent the components from coming into contact with oxygen).
<number>

## Slide 128: SG Chemistry during Inactive Periods
The five conditions in which the generator can be placed, in order of preference, are:
1. Steaming
2. Hot lay-up
3. Cold lay-up
4. Partial drain
5. Dry lay-up
<number>

## Slide 129: SG Chemistry during Inactive Periods
Lay-up condition exists when the generator is completely filled, but not steaming.
Hot lay-up => the temperature of the water is greater than 250°F.
  the pressure is high enough to prevent oxygen in leakage
Cold lay-up => the temperature of the water is less than 250°F.
  Any oxygen entering is removed by the scavenging action of carbohydrazide.
<number>

## Slide 130: SG Chemistry during Inactive Periods
Sometimes, the steam generator must be partially emptied or completely emptied for inspection.
  This is undesirable because the steam generator will come into contact with oxygen.
  The localized concentration of chemicals also cannot be controlled during dry layups.
  A dry generator is placed in cold lay-up by filling with feedwater while simultaneously injecting the lay-up chemicals.
  Nitrogen is injected through the blowdown line to provide chemical mixing and to purge air.
<number>

## Slide 131: Chemistry Control
In order to obtain a license to operate a nuclear power plant, a utility must submit a proposed set of Technical Specifications to the Nuclear Regulatory Commission.
According to Title 10 of the Code of Federal Regulations Part 50, “Domestic Licensing of Production and Utilization Facilities,” all regulations as well as the design basis of the regulations must be included in the proposed Technical Specifications.
The Technical Specifications for primary plant chemistry control include limits on chemical concentrations and activity.
These limits ensure that radiation levels in the exclusion area and low population zone do not exceed the limits of 10 CFR Part 100 under accident conditions.
<number>

## Slide 132: RCS chemistry Technical Specification
<number>

## Slide 133
<number>
Figure CR2.2 was removed.

## Slide 134: Radiochemistry Technical Specifications
Technical Specifications are essentially those numbers and conditions that were used in proving plant safety in the analysis of worst case potential accidents.
As a rule, Technical Specification Bases discuss one aspect of the relevance of the Technical Specifications limit to a worst case situation.
The RCS activity is limited to ensure that accident radiation doses are not more than a small fraction of the allowable values in 10 CFR Part 100.
<number>

## Slide 135: Examples of Radiochemistry Technical Specifications Scenarios
The worst case conditions included in the basis of this Technical Specification are the case of the failure of a Steam Generator tube at the same time that there is already a 1 gpm primary to secondary system leak.
Similarly, the 0.1 microcurie per gram steam generator activity limit also considers the effects of a 1 gpm primary to secondary system leak and the event of a steam line break.
In a Steam Generator Tube Rupture, RCS coolant fills and pressurizes the S/G until the safety valve lifts
  both RCS and S/G activity must be limited.
The Technical Specification limits the primary to secondary leakage rate.
  For example, the total allowable leakage into all the steam generators must never exceed 1 gpm.
<number>

## Slide 136: Radiochemistry Technical Specifications
There are no specific Technical Specification limits for Steam Generator chemistry.
No steam generator can have a leak rate of more than 150 gallons per day.
The Technical Specification Basis for the 150 gpd limit states that even this magnitude of defect can still ensure that the integrity of an affected steam generator tube is maintained during the abnormal differential pressures that might occur during a Steam Line Break or Loss-of-Coolant accident.
Plant chemistry control is used to prevent corrosion. Corrosion is what will lead to a 150gpd leak.
Other Technical Specifications apply to the wear and corrosion of a steam generator.
  However, the parameters of concern (tube wall thickness) must be measured during major shutdown periods.
<number>

## Slide 137: Water Purification Process
Three steps:
  Mechanic Filtration to remove solids
  Demineralizing using ion exchange resins (removes ionic impurities) and solids are also removed by the resins
  Gas Stripping – to remove dissolved gases.
<number>

## Slide 138: Chemical Additives
Used to control the conditions in the steam generator.
  Methoxypropylamine (MPA), Carbohydrazide, ammonium chloride and ammonia.
    MPA is used for pH control,
    Carbohydrazide is used to scavenge oxygen
    ammonium chloride is used to reduce stress corrosion cracking in crevice area of the Steam Generators.
<number>

## Slide 139: Chemistry of the Steam Generator Summary
Blowdown and proper chemical content of the water are effective means of maintaining steam generator integrity during normal plant operation.
<number>

## Slide 140
Briefly EXPLAIN the term Average Disintegration Energy in terms of the characteristics of the isotopes represented.
  For example, if a sample contains 2 μCi of a 1 Mev emitter and 1 μCi of a 4 Mev emitter, the weighted average energy emitted would be:
<number>

## Slide 141: Use of Hydrogen Peroxide in a Nuclear Plant
Used during plant shutdown to force the oxidation and dissolution of activated corrosion products deposited on the fuel.
Hydrogen peroxide injection, absorbs hydrogen to create water. This can be used to reduce the level of hydrogen however it relies on the use of real-time instrumentation for precise feedback on oxygen and hydrogen levels within the RCS. It has been demonstrated that rather than a 24 hour shutdown window, it is possible to complete this step within a two hour window (four hours being the adopted norm by tracking oxygen and hydrogen real-time within the reactor). This significantly reduces plant shutdown timeframes while balancing safety and maximizing operator control of the shutdown process. 1
Additional hydrogen peroxide is added to the reactor coolant to provide for controlled oxygenation of the reactor coolant and oxidative decomposition of corrosion product deposits (including activated corrosion products) then residing on surfaces of the RCS 16 and the fuel assemblies.2
Hydrogen peroxide also oxidizes organic compounds. Organic compounds such as picolinic acid, formic acid or EDTA in the reactor coolant are oxidized in the presence of hydrogen peroxide to produce carbon dioxide and ammonia.
Hydrogen peroxide is added to strip metal surfaces and the activated adhesive film is not removed. The intent of such chemical “shocking” is to pre-emptively remove crud that could increase overall radiation levels. (summary of CR2HO7)
<number>
1. http://www.engineerlive.com/Power-Engineer/Nuclear_Power/Safely_accelerating_shutdown_while_maximising_revenues/21087/
2. http://www.patentstorm.us/patents/6944254/description.html

## Slide 142: Objectives: Primary Plant Chemistry Control
Prevent the failure of reactor plant materials or equipment by destructive mechanisms of corrosion.
Minimize the thermal and hydraulic effects of crud production and deposition.
Control the concentration of radioactive nuclides to limit exposure to plant personnel and the general public.
Control reactivity throughout the life of the core. (By using boric acid.)
Identify and minimize fuel element failure.
Ensure the quality of the reactor coolant is maintained.
<number>

## Slide 143: What are the principal chemicals added to the reactor coolant during normal operations? State the reason for each.
Hydrogen
Hydrazine, H2NNH2
  Oxygen Scavenger
Boric Acid
  Reactivity in the reactor (control the rate of reaction – reduce neutron flux)
Lithium Hydroxide
  pH control
<number>

## Slide 144: What are the purposes of chemical sampling and analysis?
To ensure proper chemical makeup or detect any discrepancies in the primary system, the coolant is sampled and analyzed with specified frequency.
  Some of the chemistry-related variables the analysis will determine are dissolved oxygen, hydrogen, lithium, chloride, and boric acid concentrations.
  Sampling also measures total suspended solids, total dissolved gases, pH, and solution conductivity.
  As mentioned before, radiochemistry variables that are checked are Dose Equivalent I-131 and E-bar.
<number>

## Slide 145: What are the objectives of secondary system chemical control?
Prevent the failure of secondary plant materials or equipment by destructive mechanisms of corrosion.
Minimize the thermal, hydraulic, and clogging effects of sludge production and deposition.
Minimize effects on turbine due to carryover from the steam generator.
Ensure the quality of the secondary water is maintained.
<number>

## Slide 146: What are the two processes in the reactor coolant resulting in the production of radionuclides that cause significant radiation fields?
The first source is the activation of the water or impurities introduced with the water, such as corrosion products or chemical additives.
The second source of radioactivity is the release of radioactive fission products from the fuel or fuel cladding.
<number>
Page 7

## Slide 147: EXPLAIN the function of an ion exchanger.
The ion exchange resin has loose ions that are exchanged with the ions in solution. Examples of cations: Lithium, Sodium, Hydrogen, Magnesium, potassium. When the cation used is hydrogen, then the end result is that all the cations are replaced by H ions.
The ion exchange system also has an anion exchange portion. This replaces the anions in water by the anion loosely attached to the resin. If the anion used is hydroxide (OH-) and the cation exchanged is a proton the end result is a fully demineralized water (ion free water).
That does not mean that the water does not have metals or other non-ionic impurities. The ion exchanger will only remove ionic compounds.
<number>

## Slide 148: DESCRIBE two hazards associated with secondary (steam plant) corrosion.
Excessive buildup of general corrosion products interferes with operation of pumps and valves.
Specific local corrosion has caused the failures of several steam generator tubes.
<number>

## Slide 149: STATE the function of ammonium chloride as a chemical additive to the secondary system.
to reduce stress cracking corrosion in the crevice areas.
<number>

## Slide 150: LIST in order of ascending or descending preference the five possible conditions of a steam generator for chemistry control. (during shutdown conditions)
1. Steaming
2. Hot lay-up
3. Cold lay-up
4. Partial drain
5. Dry lay-up
<number>

## Slide 151: STATE the basis for the RCS Activity Technical Specification
Sets limits to ensure that radiation levels in the exclusion area and low population zone do not exceed the limits of 10 CFR Part 100 under accident conditions.
<number>

## Slide 152: STATE the chemicals that are added to the Primary System
Hydrogen
Hydrazine
Lithium Hydroxide
Boric acid
<number>

## Slide 153: Problem: When oxygen-16 is bombarded by a neutron, the resulting reaction causes radiation which is a major consideration in shielding requirements. Write out the reaction, and explain why the radiation occurs and why it is of concern.
The most prevalent isotope of oxygen is oxygen-16 with an abundance in nature of 99.758 percent. When bombarded by a neutron, oxygen-16 transforms to nitrogen-16:
Nitrogen-16 decays to oxygen-16 by emitting a beta minus particle and a gamma ray.
The energy of the gamma is 6.13 MeV and the half life of nitrogen-16 is 7.1 seconds.
Nitrogen-16 is one of the greatest radiation hazards in the primary system because they are a great number of oxygen-16 in the system.
Shielding requirements for the Reactor Coolant System are primarily based on the energy of the gamma produced in this reaction.
<number>

## Slide 154
What decay will take place with N-13? Beta Plus
What decay will take place with Uranium-238?
Aluminum-26 is the only stable isotope of aluminum. Predict how aluminum-24 and aluminum-30 will decay?
Al-24 – beta plus
Al-30 –beta minus
<number>

## Slide 155
Polonium was discovered in uranium ores by Mary and Pierre Curie. Polonium-210 decays by emitting an alpha particle. Write the nuclear reaction for this decay.
Write the nuclear reaction for the decay of phosphorous-32 to sulfur-32 by beta emission.
What decay will take place with Uranium-228?
What decay will take place with Cu-68?
Oxygen-16 in the presence of a nuclear flux, it reacts to produce a nitrogen isotope. What is the danger associated with this reaction?
<number>

## Slide 156
Book available online for free:
http://www.nap.edu/catalog.php?record_id=9263
<number>